Leader’s Guide

# Table of Contents

| Class Kick-off and Introduction | 3 |
| --- | --- |
| Jetson System Overview | 7 |
| Customer Communication - Arriving on Site | 15 |
| Line Set Unrolling | 25 |
| Line Set Cutting | 29 |
| Line Set Bending | 35 |
| Line Set Press Fitting | 39 |
| Line Set Flaring | 44 |
| Service Valve Flare Nut Torquing | 48 |
| Removing Old Condensing Unit | 52 |
| Removing Old Forced Air Unit | 59 |
| Building Plenum Transitions | 63 |
| Building Base Cans | 68 |
| Installing Sensors | 73 |
| Installing the Condensate Pump | 78 |
| Building the Base Pad and ODU Stand | 84 |
| Line Set Cleaning | 89 |
| Nitrogen Pressure Testing (3, 4, & 5 Ton) | 94 |
| Vacuum Testing (3, 4, & 5 Ton) | 102 |
| Charging the System (3, 4, & 5 Ton) | 108 |
| Nitrogen Pressure Testing (2 Ton) | 114 |
| Vacuum Testing (2 Ton) | 121 |
| Charging the System (2 Ton) | 127 |
| Wall Penetrations and Line Set Routing | 132 |
| Wiring the Jetson Smart System | 143 |
| Provisioning the Jetson Hub | 149 |
| Commissioning the System | 157 |
| Customer Communication - Departing the Site | 164 |

## Jetstart Training Class Kickoff and Icebreaker

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

60 - 90 minutes

Group Size

Whole Class

Class Kick-off & Introductions:

Instructor presentation:

“Welcome to Jetstart Installation Training! This training is designed to provide you with the necessary training to start working with your crew and install Jetson Air System on customer’s homes.”

Instructor presentation:

- Pair students up

- Ask them to interview each other with questions below (give them 5 mins)

  - Their name

  - Their job title,

  - Their location,

  - Their walk-on music

  - One thing they want to learn during the training. (Okay to have repeats)

- Have the students introduce each other to the class.

- Instructor captures the walk-on music and the learning objective on white board/flip chart

- Throughout the training:

  - Play the walk on music during breaks and hands-on activities

  - Cross off learning objectives as you cover them in class

Agenda

Instructor presentation:

- What to expect during this training class

- Provide a high level overview of the topics we’ll cover over the next 10 days

- You’ll learn:

  - Who is Jetson as a company

  - How the entire Jetson Air System works

  - How to remove old HVAC systems from customer’s homes

  - How to unroll, cut, bend and attach line sets

  - How to install every piece of the Jetson Air System

  - How to pressure and vacuum test systems to ensure their ready for installation

  - How to charge Jetson Air System with refrigerant

  - How to start up and test the Jetson Air System to ensure they’re installed correctly.

- Class will begin everyday at 7:00

- You get 15 minute breaks and a 45 min lunch break

- We’ll end the day around 3:45

Who is Jetson?

Instructor presentation:

- Jetson background

- Our Vision

  - To create a future that’s 100% electric and 100% better—one expertly upgraded home at a time.

- Our Mission

  - Together, we’re accelerating the switch to clean, all-electric homes across North America. As a Jetson installation partner, you help make the electric home not just possible—but effortless. With every install, you’re not just wiring a unit—you’re wiring in the future of home energy.

  - We bring the tech, the tools, and the trust. You bring the craftsmanship. And together, we deliver a seamless, single-day switch that homeowners rave about.

- Upper management/founders

- Locations

Code of Conduct

Instructor presentation:

- How we treat our customers

- How we treat our co-workers

- Expectations for working on site:

  - 8 AM at the customers job site

  - Parking in the correct spot.

  - Wear Jetson uniforms (briefly review dress code expectations)

  - Roll out Jetson runner mats in home between entry point and work area

  - Keep work areas clean and tidy throughout the day

  - Keep interactions with homeowner friendly

  - Introduce yourself at the beginning of the day, make sure they are aware of the scope of the work, and ask permission to place a Jetson Sign on front yard

- Working safely and wearing PPE

- During training, and on future job sites, whether you are wearing the Jetson brand or not, you’re representing Jetson and will be held responsible for any bad behavior, up to and including dismissal.

Training Facility Tour

Instructor presentation:

- “Let’s make sure that everyone is familiar with the training facility and where everything is located.”

  - Get the students out of the seats and out of the classroom

- Ensure the students know where the restrooms are located

- Ensure the students know where the break room is located

- Walk the group into the hands-on lab area and give them a brief introduction of the lab stations, explaining briefly what they will be doing in this lab, with these stations during the rest of their time in training.

- Walk the students to the Jetson “truck” tool cages so that they can see how the tools are organized.

- Inform the students that the tool cages have been set up just like the back of the truck. As they work through the classroom activities, they’ll take the group of systainer kits necessary for each activity out, then make sure all the systainer kits are put back in the tool cage before taking the next set out.

- Let them know that throughout their training, they’ll have tool buckets with all the necessary tools. It’s their responsibility to keep track of these tools during training.

Setting Expectations

Instructor presentation:

- Explain that while students may have a specific role on the job (indoor vs outdoor), JetStart teaches all (non-electrical) jobs. This equips everyone to assist with any activity throughout the installation process.

Extra Ice Breakers

Instructor note:

This additional icebreaker option can be used on day 2, another day, after lunch or for a break/change the pace to give the installers the opportunity to get to know each other better.

## “Two Truths and a Lie”

- Give everyone 2 minutes to think of:

  - 2 true facts about themselves

  - 1 lie (the more believable or ridiculous, the better)

- One person shares their three statements.

- The group votes on which one is the lie (hands up, shout it out, etc.).

- Reveal the lie—and let the person briefly explain the truths.

- Rotate through the group.

## Classroom Activity: The Jetson System Overview

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

90 minutes

Group Size

Entire Class

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify all major Jetson Air System components

- Identify the HVAC components being replaced by the Jetson Air System

- Describe the function of each component

- Explain how components interact during heating and cooling modes

- Recognize common installation considerations and failure points

- Describe the difference between a 2, 3, 4 and 5 ton Jetson Air System

## Materials & Tools

- Complete Jetson Air System in the classroom/lab area

### Activity Part 1: The Big Picture (15 minutes)

Walk the class over to the Jetson Air training system in the training area.

Instructor explains:

- Introduce the class to the Jetson Air System

  - Initially only provide a high level introduction

  - “This is a complete, installed system.”

Group discussion:

- “Is a heat pump a heater, an air conditioner, or both?”

  - A heat pump moves heat, it doesn’t creates it

  - In cooling mode, it moves heat out of the home

  - In heating mode, it moves heat into the home

- “Are all heat pumps the same, or are there different sizes?”

  - Jetson sells 2, 3, 4 and 5 ton units

- “Can anyone explain what a ton is?”

Instructor explains:

- “Now we’ll dive deeper into each of the components of the Jetson Air System, what each component does, and how they all work together.

### Activity Part 2: The Outdoor Unit (15 minutes)

Instructor explains:

- “We’re going to start outside and work our way into the home.“

- “This is the outdoor unit, or you’ll hear it called the ODU”

  - Explain what the ODU does (condensing unit)

  - Explain the purpose of the base/pad and the stand

  - Explain wall bracing for safety

  - Discuss the connections to the line sets on the side of the unit

  - Discuss the electrical connections on the ODU (whips and disconnect)

- “Some of you are from some areas of the country where the weather gets pretty cold, the outdoor units that we install are cold weather units. We can install these in very cold climates and they still work extremely efficiently.”

### Activity Part 3: The Line Sets (5 minutes)

Group discussion:

- “Does anyone know what the line sets do?”

- “Can someone explain why the line sets are two different sizes?”

Instructor explains:

- The two different sizes of line sets:

  - Liquid Line (smaller):

    - Carries high-pressure, warm liquid refrigerant from the outdoor unit (condenser) to the indoor unit (evaporator) in the cooling mode

  - Suction Line (larger, insulated):

    - Carries low-pressure, cool gaseous refrigerant from the indoor unit back to the outdoor unit condenser in the cooling mode

    - This line is insulated to prevent heat gain (in cooling mode) or heat loss (in heating mode) and reduce energy waste

  - In heating mode, the cycle reverses

- When (or if) we’re able to reuse existing line sets from their previous HVAC system vs. when we need to run new line sets

- The purpose of the insulation on the line sets

- The purpose of line hide and when to use it

### Activity Part 4: The Indoor Unit  (15 minutes)

Instructor explains:

- “Now we’re going to follow the line sets from the outdoor unit inside to the indoor unit 
or IDU.”

- The IDU can be in a variety of places inside a home

  - Attic - Typically in a horizontal position

  - Crawlspace - Typically in a horizontal position

  - Unfinished or finished basement - Upflow or down flow position

  - Closet/central location - Upflow/downflow position

- “This is the indoor unit, or you’ll hear it called the IDU”

  - Explain what the IDU does (evaporator unit)

  - Explain the purpose of the return base can and plenum

  - Show the line sets connecting to the IDU

  - Discuss the connections to the line sets on the side of the unit

  - Discuss the different ways line sets may need to be routed from the ODU depending on the location of the IDU

  - Cover the different configuration the coil and drain pan need to be in when changing from upflow to horizontal left or downflow

  - Explain the purpose of a condensate pump

Group discussion:

When going over the components of the indoor unit, ask for participation to see if any of the installers have familiarity/experience with heat pumps.

- “Is anyone familiar with a heat pump system?”

- “Can someone explain what the air handler does?

  - The main indoor cabinet that houses the components and pushes air into the ducts.

- “Can someone explain what an evaporator coil is, and what it does?’

  - This coil absorbs heat from indoor air (cooling) or releases heat into it (heating) and also dehumidifies.

- “What does the blower fan do?”

  - Circulates air across the coil and through the duct system.

- “What’s the purpose of the air filter?”

  - Cleans the air as it passes through.

- “How often should the homeowner replace their airfilter?”

- “What is a heat strip?”

  - Provide an overview of what the heat strip is for.

- Do we always install heat strips in the indoor unit?

  - Provide reasons why we install them vs don’t install them.

  - Explain that we install cold weather systems but sometimes they need a boost.

### Activity Part 5: The Jetson Hub and Sensors (20 minutes)

Instructor explains:

- “Now we’ve talked about the main mechanical components of the system, let’s take a look at the electrical equipment and sensors for the Jetson Air System.”

- “We’ll start with the Jetson Hub.”

  - Explain the purpose of the Hub and what it does

  - How it communicates (Wi-Fi)

    - Antennas (long vs short)

- “Next, this is the Temperature and Humidity Sensor.

  - This is a single sensor that measures both temperature and humidity.

  - It’s installed in the supply duct or AHU heat strip cavity, upstream of any strip heat, before any branches in the ducting.

  - It’s hard‑wired to the Jetson Hub on the SEN terminals (power, ground, RS‑485 +/–), so the Hub continuously reads its data.

  - Reasons for measuring the supply air temperature:

    - Confirms what air is actually leaving the system.

    - Lets Jetson monitor whether the system is heating/cooling as expected and catch issues (e.g., underperforming heat, overheating supply air, etc.).

  - Reasons for measuring the supply air humidity:

    - Tracks how the system is affecting indoor moisture levels.

    - Provides input for system health/comfort monitoring and future insights in the app (alongside the AQI and energy sensors referenced in product materials).

  - Together the Hub uses these readings (along with IAQ and energy sensors) so Jetson can monitor performance 24/7, detect abnormal behavior early, and support troubleshooting.”

- “This is the Indoor Air Quality Sensor also known as the IAQ. The Indoor Air Quality Sensor in a Jetson system is a duct‑mounted indoor air quality probe wired to the Jetson Hub. It’s installed in the supply duct, with its slits aligned to airflow, and connected to the hub’s SEN terminals (power, ground, RS‑485 +/–).

  - Functionally the IAQ does three things:

- Measures what’s in your air:

  - Continuously samples supply air for indoor air quality metrics (e.g. CO₂, dust, pollen, cooking particles / fine particulates).

- Feeds data to the Jetson Hub for 24/7 monitoring:

  - The hub uses IAQ sensor data (along with energy and temperature/humidity sensors) to:

  - Watch for abnormal or degraded air quality.

  - Support remote diagnostics and performance checks as part of Jetson’s 24/7 monitoring.

- Enables air-quality insights and filter‑related behavior:

  - That sensor data underpins air quality insights in the Jetson system and supports things like:

  - Notifying when air quality degrades (e.g. cooking events, dust, pollen spikes).

  - Supporting “cleaner air” features such as filter‑change reminders and future automations that react to poor air quality.

  - So in short: the IAQ Sensor is how Jetson “sees” what’s in the air the system is delivering, so monitoring and software can catch issues, surface insights, and eventually automate around indoor air quality.”

- “Also connected to the hub, but mounted inside the main electrical panel is the Emporia.” In a Jetson Air System, the Emporia device is the energy monitor.

  - It’s used to:

- Measure real-time electrical usage:

  - A current transformer or CT clamp on the panel to measure how much power the outdoor unit (ODU) is are drawing

  - That data is tied to the Jetson system so usage can be tracked per system.

- Feed data into Jetson’s monitoring stack:

  - The Emporia monitor sends power data that Jetson uses for 24/7 performance and health monitoring, alongside temp/humidity and AQI sensors.

  - It helps flag abnormal power draw (e.g., short cycling, stuck heat strips, or compressor issues) and supports remote diagnostics.

- Enable energy insights and future optimizations:

  - The energy monitor is the hardware backbone for energy-use insights and future features like optimization around time-of-use rates and demand response events, to reduce bills and improve efficiency.

  - The Emporia is how Jetson “sees” exactly how much electricity your system is using, in real time, so monitoring and software can catch issues, understand performance, and eventually help optimize costs.”

- “Next we have the thermostat. The Jetson Thermostat offers simple, intuitive control over your home’s temperature, with visual indicators for mode, temperature, fan, and status.”

- “Lastly, there is the Jetson Homeowner app. The homeowner app provides the same advanced functionality as the wall-mounted thermostat but available on a mobile device.”

### Activity Part 6: Watch Heat Pumps Explained Video (5 minutes)

Video:

Have the class watch the video how heat pumps work (PPT slide #X)

- Heat Pumps Explained - How Heat Pumps Work HVAC

  - Start video at :55 and watch to 5:30

Group discussion:

- Review all the components in a heat pump system

  - Outdoor unit & coil

  - Indoor unit & coil

  - Line sets

### Activity Part 7: How Everything Works Together (25 minutes)

Group discussion:

“Now that we’ve talked about all of the parts of a complete Jetson Air System, let’s discuss how everything works together to heat and cool the home.”

Ask prompting questions to encourage group discussion and participation when discussing the following:

- Outdoor Unit:

  - What does the Outdoor Unit, or ODU do?

    - The compressor pressurizes refrigerant, turning it into a hot, high-pressure liquid that travels to the indoor unit via the liquid line.

- Line sets:

  - What do each of the line sets do?

  - How do we protect the line sets?

- Indoor Unit:

  - What does the Indoor Unit, or IDU do?

    - The liquid refrigerant expands and absorbs heat from your indoor air, turning into a cool gas.

- The Jetson Air System:

  - “What happens if you reverse the direction that a heat pump operates?”

    - A heat pump reverses this process to provide heating, essentially acting as a reversible air conditioner, moving heat from outside to inside or vice versa. The line set is crucial for this continuous heat transfer.

## Assessment

Ask for volunteers to answer verbally:

- "Pick one component and explain what it does as if you were talking to a homeowner."

## Key Takeaways

- Every heat pump has three major functions:

  - Airflow

  - Refrigerant movement

  - Jetson Smart System - Sensors, controls, and monitoring

- Good installers understand what each part does and how their installation affects it

- Knowing how everything works together will help streamline your installation process

- Knowing how the system operates will help you troubleshoot issues faster

## Role-Play Activity: Jetson Installer Meet & Greet

### Target Audience

New Jetson installers

### Duration

60 minutes per group

## Presentation Deck - (Slides XX)

## Learning Objectives

By the end of the activity, the installer will be able to:

- Introduce themselves and their crew confidently and professionally to the homeowner

- Confirm the scope of work in simple terms

- Set expectations for time, noise, access, and cleanliness

- Ask for parking recommendations

- Ask where they can place old equipment until they take it away

- Ask for bathroom privileges

- Complete the job pre-walk with customer and discuss:

  - Equipment location

  - Line set/linehide runs

  - Cutting holes in ceilings and walls

- Ask homeowner for Wi-Fi credentials

- Ask respectful clarifying questions

- Respond calmly to basic homeowner concerns

## Setup (Instructor Prep)

- Print out the scripts for the learners the day before this activity

- Assign homework that the installers should work in small groups to discuss and practice the scripts before class

- The installers should be prepared to role-play the scripts in class

## Roles

- Installer

- Homeowner

- Observer / Trainer / Classmates

Rotate roles so everyone practices being the installer.

Scenario Setup

Each one of you will get to play the part of the Lead Installer. You’ll do all the things that the Lead is supposed to do, from introducing yourself and your crew to the homeowner to explaining to the homeowner where your team is going to place the IDU and the ODU and run the line set, to what will happen if you have to cut holes in the ceiling.  This is your opportunity to practice leadership and communication skills.

Background given to installer:

- You are installing a new Jetson Air System

- You have arrived on time, in uniform, with tools

- This is your first interaction with the homeowner today

Background given to homeowner:

- You’ve never met this installer

- You may be curious, cautious, or unsure what will happen today

- You have a few common homeowner concerns

## Role-Play Steps

### Step 1: Door Knock & Introduction

Installer practices:

- Knocking or ringing bell

- Stepping back from the door

- Friendly greeting and eye contact

- Name, company, and purpose of visit

Instructor listens for:

- Clear introduction

- Polite tone

- Professional body language

### Step 2: Confirming the Job & Expectations

Installer should:

- Briefly explain what work will be done today

- Confirm equipment location(s)

Instructor listens for:

- Accurate explanation of the work being performed

- Polite tone

- Professional body language

### Step 3: Safety & Home Protection Brief

Installer should:

- Ask permission before entering the home

- Explain that you’ll be putting down tarps, runners and wearing boot covers

- Set expectations for:

  - Duration of work

  - Noise

  - Power interruptions

  - Driveway access

  - Thermostat changes

  - Cleanup

Instructor listens for:

- Accurate explanation of how the crew will protect the home while working in it

- Polite tone

- Professional body language

### Step 4: Detailed Step-by-Step Installation Plan

Installer should:

- Thoroughly explain the full day’s work flow

- Explain line set runs

- Explain indoor and outdoor unit work

- Explain installation of the Jetson Air System

- Explain the various system tests

- Let the customer know that once the work is complete, you’ll walk them through all of the completed work, review how to use the system, thermostat and Jetson app

Instructor listens for:

- Accurate explanation work performed

- Polite tone

- Professional body language

### Step 5: Access & Logistics Check

Installer should:

- Let the customer know that before they begin work, they’d like to confirm a few logistics for the day

- Ask for the Wi-Fi password so that you can connect their smart system to Jetson’s monitoring system

- Ask if there are any pets to be aware of

- Ask if there are any areas to avoid or be extra careful around

- Explain where the new equipment will be staged

- Ask the homeowner where you can put the old equipment until the end of the day, 
when they will load it in the truck and dispose of it.

- Ask the customer where they should park their vehicles

- Ask permission for use of the customer’s bathroom

Instructor listens for:

- Asked for any special considerations the crew should be aware of

- Ensured where the crew can stage both old and new equipment

- Politely asking permission to use the bathroom and where to park their vehicles

- Polite tone

- Professional body language

### Step 6: Communication & Point of Contact

Installer should:

- Let the Customer Know You’ll Be Their Point of Contact Throughout the Entire Process

- Ask Permission to Post the Jetson Yard Sign in Their Front Yard

Instructor listens for:

- Polite tone

- Professional body language

### Step 7: Close with Confidence

Installer should:

- Confirm with the customer that everything sounds good

- Let the customer know that they’re excited to get started

- Remind the customer that when they finish, they’ll show them how to operate and maintain their system

- Ask the customer if when you’ve they’re comfortable giving us a 5 star Google review if they’re happy with your work

Instructor listens for:

- Enthusiasm

- Polite tone

- Professional body language

### Homeowner Questions & Concerns

Homeowner asks 2–3 of the following (choose randomly):

- “How long will this take?”

- “Will there be a lot of noise?”

- “Do I need to be home the whole time?”

- “Will you be going in the attic?”

- “Is there anything I should move or cover?”

- “Who do I talk to if I have questions later?”

Instructor listens for:

- Installer clearly answers without jargon

- Installer stays calm and confident

- Installer avoids oversharing or guessing

- Installer shows respect for the home

## Observer Evaluation Checklist

Rate each item: Great Job or Needs Work

- Clear introduction (name + company)

- Friendly, respectful tone

- Explained work simply

- Set expectations clearly

- Explained how the crew will protect the customer’s home

- Asked permission before entering

- Asked where they should park their vehicles

- Asked if they could have access to the customer’s bathroom

- Responded calmly to questions

## Debrief Discussion (5 minutes)

Ask the group:

- What felt natural?

- What felt awkward?

- What phrases worked well?

- What could build more trust?

- How would this change for a nervous or upset homeowner?

## Advanced Variations

- Homeowner is rushed or distracted

- Homeowner is skeptical or unhappy from past construction projects

- Lead Installer must explain a delay or unexpected issue

- Lead installer must explain that the installation requires cutting holes in the ceiling/wall that Jetson does NOT repair.

- Lead Installer greets homeowner with pets or kids present

## Scripts - (In the participant’s Training Manual)

### Step 1: Door Knock & Introduction

“Good morning! Hi, I’m [Name], the lead installer with Jetson Home. We’re here to install your new heat pump system today.

Before we get started, I’d like to walk you through what today will look like, introduce you to the crew, and answer any questions so there are no surprises.

Is now still a good time for you?

(Pause - confirm permission)

### Step 2: Confirming the Job & Expectations

“Just to confirm, today we’ll be installing:

- [Heat pump system type]

- Indoor unit located [location]

- Outdoor unit located [location]

- The Jetson Air System, any electrical upgrades or disconnects that the [Name], your Electrification Consultant discussed

Our goal is to have everything installed, tested, and cleaned up by approximately [time range], barring anything unexpected.”

### Step 3: Safety & Home Protection Brief

“A couple of things to set expectations inside your home:

- We’ll lay down floor protection and drop cloths in all work areas, and we’ll wear floor protectors while in your home.

- Power may be temporarily shut off at certain points for safety

- If you’re here, we’ll let you know when the electricity will be 
turned off.

- You’ll hear drilling and equipment noise at times.

Safety is our top priority—for you, your home, and our crew.”

### Step 4: Detailed Step-by-Step Installation Plan

“Here’s how today will flow, step by step:

First, we’ll stage equipment and prep the work areas.

Second, we’ll remove your old equipment and put it [place that they pointed out]

Third, we’ll install the indoor system and run any necessary refrigerant, drain, or electrical lines.

Fourth, we’ll install the outdoor unit and complete all electrical and refrigerant connections.

Fifth, we’ll install the Jetson Air System.

Sixth, we’ll test the system, balance airflow, and confirm performance in heating and cooling modes.

Finally, we’ll walk you through how to use the system, review the thermostat, the Jetson App and answer any questions before we leave.”

### Step 5: Access & Logistics Check

“Before we begin, I just want to confirm a few logistics:

- We will need your Wi-Fi password so that we can connect your Jetson Smart System to our monitoring system.

- Are there any pets we should be aware of or keep doors closed for?

- Are there any areas you’d prefer we avoid or be extra careful around?

- Where’s the best place to park and stage equipment?”

### Step 6: Communication & Point of Contact

- “I will be your point of contact if you have any questions or concerns throughout the entire installation process. Feel free to speak directly to me at any point today.

- If it’s okay, we'd like to post one of our Jetson yard signs in front of your house to let all of your neighbors know that you had a new Jetson Air System installed in your home today. Would that be okay with you?”

### Step 7: Close with Confidence

“If everything sounds good, we’ll get started.

We’re excited to get you set up—this system should make your home more comfortable, more efficient, and future-ready.”

Now that the homeowner is particularly engaged:

“At the end of the day, I’ll also show you how to:

- Optimize comfort settings

- Understand energy usage

- Know when and how to maintain the system

We want you to feel confident owning it—not just using it. The goal of my team is to provide you with 5 Star Jetson Experience, and trust that you would be comfortable giving us a Google Review if we live up to your expectations.”

## Hands-On Activity: Line Set Unrolling

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

60 minutes

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Explain why improper unrolling damages a line set

- Correctly unroll a coiled line set without causing kinks or flat spots

- Identify common unrolling mistakes and how to correct them

- Inspect a line set for damage after unrolling

## Materials & Tools

- (4) coiled copper line sets (⅜” and ¾”)

- Open floor space (minimum 25 ft)

- Tape measure

- Utility knife

- Marker, cones, or tape (to mark walking path)

- Electrical tape

- Scrap/damaged copper (for demonstration)

- Safety gloves and glasses

### Activity Part 1: Theory & Tool Overview (5 minutes)

Instructor explains:

- Show a rolled up line set and explain that they come rolled up from the factory.

- Explain that it’s important to properly unroll the line sets to avoid:

  - Damaging them

  - Damaged line sets don’t look good

  - Messing with damaged line sets/trying to fix them wastes time on the job site

  - Overworked copper - soft copper hardens the more you work it and becomes difficult to bend and flare later.

- Show a kinked or flattened copper tube and explain:

  - Oil return issues

  - Refrigerant flow restriction

  - Increased compressor wear

  - Potential leaks and callbacks

### Activity Part 2: Incorrect Method (10 minutes)

Instructor explains:

Common mistakes when unrolling line sets:

- Pulling the coil straight up

- Throwing the coil across the floor

- Letting the coil spring open

- Dragging the coil sideways

Group discussion:

- “What do you think will happen inside of the line set?”

- “Why do we want to reduce/minimize bending and adjusting soft copper?”

### Activity Part 2: Correct Unrolling Method (5 minutes)

Instructor-led demonstration

- Hold the line set coil

- Gently stand on the loose end of the line set coil

- Hold the coil and walk in small increments keeping the coil straight as possible

- Gently step on the line set to hold it and continue to walk in a straight line

  - Allow the coil to roll and open naturally

- Keep the line set:

  - Perpendicular to the floor

  - On flat ground to avoid unnecessary bends

  - On smooth ground to avoid damaging the line set

Always ensure that your foot is on the line set as you unroll and keep the roll 90 degrees to the ground, follow a straight line, and always unroll on flat ground.

## Activity Part 3: Hands-On Practice (20 minutes)

Activity Setup

- Give each group (2 installers) one coiled line set

- Each group of two will unroll 21’ of the 50’ coil

- Mark a straight walking path with tape or cones

Installer groups should work together to complete the following:

- Each group must:

- Inspect the coil before starting

- Properly unroll the entire line set (21’)

- Lay it straight on the floor

- Perform a final visual inspection

### Checkpoint:

- Stop anyone immediately if they force the line set

- Ask them why they think they were stopped or adjusted

- Reinforce smooth, controlled movement

## Activity Part 4: Inspection & Problem Solving (15 minutes)

### Group Inspection

Neatly remove the line set insulation and lay all unrolled line sets side by side and inspect for:

- Kinks

- Flat spots

- Uneven bends

- Stress marks

NOTE: Remind the class that this was a classroom activity. Never remove line set insulation and inspect the line sets in the field.

### “Fix or Fail” Challenge

Show slightly damaged line sets and ask:

- “Is this usable?”

- “Where would this cause issues?”

- “Should it be replaced or repaired?”

- “How would you repair the line set?”

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Not unrolling on smooth ground (avoid rough/rocky ground)

- Pulling on the coil/Not walking the coil open

- Not stopping at the first sign of resistance

- Damaged copper means:

  - System problems later

  - Ugly line set runs

## *Instructor Note*

- The following activity will be line set cutting. Use the (4) 50 ft. coils that were unrolled in this activity to use in the cutting activity.

## Hands-On Activity: Cutting Line Sets with a Pipe Cutter

Target Audience

Entry-level to intermediate Jetson installers

Duration

60 minutes

Group Size

Individual Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Select the correct pipe cutter for copper line sets

- Measure and mark accurate cut locations

- Demonstrate the proper way to start cutting the pipe

- Demonstrate cutting copper line sets squarely without deforming/damaging the pipe

- Demonstrate deburring the inside and outside edges of the pipe

- Identify and correct common cutting mistakes

- Properly prepare line set ends for flaring and pressing

## Materials & Tools (per station)

- Unrolled line set sections from the line set unrolling activity (3/8" and 3/4")

- Standard HVAC tubing cutter HID & HOD -TB

- Utility Knife

- Electrical Tape

- Tape measure

- Permanent marker

- Deburring tool or reamer

- Safety gloves and glasses

- JIG-wooden boxes with slots that students place their pipes into to verify proper lengths

## Safety Brief

Instructor reviews:

- Eye protection and gloves are required at all times

- Copper edges are sharp after cutting

- Proper hand placement to avoid pinching

- Keep fingers clear of rotating cutter wheel

- Never over-tighten the cutter

Instructor-led demonstration:

- Show both correct and incorrect cutting techniques.

## Activity Part 1: Theory & Tool Overview (5 – 10 minutes)

Instructor asks:

- When do line sets need to be cut?

Instructor-led demonstration:

- Instructor identifies the cutter components:

- Cutting wheel (HOD & HID-TB)

- Guide rollers and groove (flaring)

- Adjustment knob

- Instructor performs a cut for the group

- Instructor demonstrates how to use the ream tool

Instructor explains:

- Why hacksaws are not acceptable for HVAC refrigerant line sets.

- Why it’s important to maintain the cutter and sharpness of the wheel.

## Activity Part 2: Measuring & Marking (10 minutes)

Each Installer completes the following:

- Measure assigned line set lengths (both 3/8" and 3/4"):

  - (2) - 4’

  - (1) - 24 ⅝”

  - (1) - 18 ¼”

  - (1) - 12 ½”

- Mark tubing clearly at the cut location

- Verify measurement with instructor before cutting

Assessment:

- Accuracy within ±⅛"

- Clearly visible marks

## Activity Part 3: Cutting Technique (15 – 20 minutes)

Each Installer completes the following:

- Place cutter on tubing at the marked line

- Tighten adjustment knob until snug (not tight)

- Rotate cutter around tubing 2–3 full turns (this creates a scoring path so the cutter doesn't spiral)

- Slightly tighten knob (¼ turn max)

- Repeat process until the cut is complete

- Catch cut tubing to prevent bending, denting, or damage

- Should have the following lengths in both 3/8" and 3/4":

  - (2) - 4’

  - (1) - 24 ⅝”

  - (1) - 18 ¼”

  - (1) - 12 ½”

- Place electrical tape over the cut ends immediately after making cuts

NOTE: These will be used in the line set routing, bending, flaring, ProPress activities

Key Coaching Points:

- Do not over-tighten

- Let the cutter do the work

- Cut largest pieces first

- Listen for smooth cutting sound (not squealing)

- If the cutter creates a spiral on the tubing, move the cutter down and start again

## Activity Part 4: Deburring/Chamfering & Inspection (10 minutes)

Instructor explains:

- How the pipe has rough edges after using the cutting tool.

- How the pipe has a rough exterior from the cutting tool moving around it.

- What deburring and chamferring is, and why it's necessary.

  - The line set edges need to be smooth so that they don’t tear the o-rings in the press fittings.

  - A rough groove from the cutting tool can allow air to leak by the o-rings in the press fittings.

Each Installer completes the following:

- Ream inside of tubing

- Deburr the outside of the tubing

- Inspect cut end for:

  - Square cut

  - No crushed or oval tubing

  - Clean interior to clear copper shavings

  - Inside and outside defects in the pipe

- line sets should always be tight, clean and dry

Instructor-led demonstration:

- Using a piece of scrap pipe, show how burrs and improperly reamed pipe can affect refrigerant flow and oil return.

Instructor explains:

- How reaming and chamferring works for flaring but is also a best practice when connecting any pipes.

- How a poorly deburred/chamfered pipe can cause

  - Turbulence and noise

  - Hissing

  - Vibration

  - Pin holes

- Why the pipe should be facing downwards when deburring.

- How to properly tap the pipe to knock the shavings out without damaging the pipe.

## Assessment

Each Installer completes the following:

- Accurate measurements

- Smooth square cuts

- Proper deburring

- Safe work habits/proper PPE use

## Common Mistakes Discussion (5 minutes)

Group discussion led by instructor:

- Over-tightening the cutter

- Crooked cuts

- Forgetting to deburr

- Using damaged cutter wheels

- Putting your finger inside the pipe (to check for burrs) before deburring. This can easily lead to cut fingers!

- Leaving any debris in the pipe can damage and ruin a system!

- Not blowing shavings out from vertical pipes after reaming. Cutting vertical pipes should be a last resort!

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## *Instructor Note*

- Use the (2) 4’ line sets cuts from this activity in the bending and press fitting activities.

- Use the (6) shorter line sets cuts from this activity in the flaring activity.

- Use the remaining 24’ from this activity in the line set routing activity.

## Hands-On Activity: Copper Line Set Bending Fundamentals

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

90 minutes

Group Size

Individual Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Identify correct bend radius for copper line sets

- Use common bending tools properly (hand, spring, lever, and ratcheting benders)

- Bend copper without kinking, flattening, or work-hardening

- Plan, measure, and mark bends to match real-world installation scenarios

- Inspect bends for quality and flow integrity

## Materials & Tools (per station)

- Pre-cut 4’ line set sections (3/8" and 3/4")

- HOD & HID - TB

- Tubing benders - VF

- Tubing cutter and deburring tool

- Measuring tape and marker

- Bend radius chart (posted or printed)

- Sample line set routing templates

- Safety glasses and gloves

- Scrap plywood or wall mock-up–will need 3-4

## Setup (Instructor Prep)

- Utilize 4’ piece of pre-cut line set

- Prepare bend challenge templates, such as:

  - 90° bend end of pipe to center of 90 - 12”

  - Offset around a joist - (2) 45°

  - Reverse bend

- Mark bend start/end points on templates or boards.

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- What line set bending is

- When it’s necessary to bend the line sets

Instructor-led demonstration:

- Correct tubing measurement and marking (proper bending radius)

- Minimum bend radius by tube size

- Common mistakes:

  - Kinking

  - Over-bending

  - Re-bending

Instructor explains:

- Quality expectations for bending line sets:

  - Clean aesthetic bends where needed

  - Any kinks should be repaired with press-fit coupling

### Activity Part 3: Guided Practice Bends (30 minutes)

Each installer completes the following:

Utilizing one 4’ piece of pre-cut line set:

- Cut line set insulation

  - Cut perpendicular to the pipe

  - Do NOT score the pipe when making the cut

  - Move enough insulation to make the bend

  - Neatly slide the insulation back in place after making the bend

  - Tape insulation seam with color matched duct tape

- 90° Bend

  - Must meet radius spec

  - Do NOT overbend past 90 degrees

  - No visible flattening

- Offset Bend

  - Two equal bends aligned correctly

  - Correct spacing and symmetry

- Reverse Bend

- Tape line set insulation

  - Neatly slide the insulation back in place after making the bend

  - Tape insulation seam with color matched duct tape

- Compare bends to wooden templates

Instructor circulates: correcting hand position, tool alignment, and bend speed.

Checkpoint: Each installer must complete at least three of each bend type.

### Activity Part 4: Real-World Bending Challenge (10 minutes)

Installers choose or are assigned a bending template:

- Measure and plan bend locations

- Mark tubing

- Complete all bends using the line bending tool

Rules:

- No re-bending allowed

- Replace tubing if kinked

- Focus on planning before bending

## Evaluation & Inspection (5 minutes)

- No kinks or sharp creases

- Tube remains round

- Correct bend angles

- Clean, professional appearance

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Scoring the line set when removing insulation

- Overbending past 90 degrees

- Kinking or flattening the line sets

## Debrief & Key Takeaways

Group discussion:

- What caused mistakes?

- How to avoid wasted tubing in the field

- Importance of planning bends before cutting

- Always try to run one continuous line (minimize press fittings)

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Installing Line Sets with an 
RLS Press Tool

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

90 minutes

Group Size

Individual Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Safely operate an RLS Press Fitting tool

- Properly prepare copper tubing and fittings

- Make secure press connections

- Inspect and test pressed joints for leaks

- Identify and correct common installation errors

## Materials & Tools (per station)

- Systainer Kit - HOD - TB

- Systainer Kit - HID - TB

- Systainer Kit - HPT

  - RLS Press Fitting  tool

  - Press jaws (3/8" and 3/4")

  - Deburring reamer/chamfer

  - Scotch-Brite pad

  - Depth gauge

  - Crimp gauge

- Systainer Kit - HPF

  - Press fittings (3/8" and 3/4")

    - (3) couplings

    - (3) 90 elbows

    - (3) 45s

- Pre-cut 4’ line set sections (3/8" and 3/4")

- Tubing cutter

- Permanent marker

- Tape measure

- Press Fitting with a damaged O-ring (for demonstration purposes)

- Safety glasses & gloves

### Safety Brief

Instructor reviews:

- PPE requirements

- Pinch-point hazards with press jaws

- Battery tool handling and storage

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- What a press fitting tool is and why we use them at Jetson

- When to use a press fitting on the job

- Press Fitting vs Brazing

  - Why we don’t braze at Jetson

  - Press fitting:

    - Creates consistent joints

    - Requires fewer tools/equipment

    - Are easier on the HVAC equipment

      - Less carbon buildup

      - Less contamination

Instructor-led demonstration:

- Identify parts of the press fit tool:

  - Trigger

  - Jaws

  - Battery - (Ensure batteries are fully charged at the beginning of the day)

  - LED indicators

- Match correct jaw size to fitting size.

- Importance of calibrating the jaws when changing sizes of jaws.

  - Cycle with new jaws once before using the press tool to recalibrate the jaws.

- Inspect fittings:

  - O-ring condition

  - Manufacturer markings

  - Correct depth indicators

  - (Show a damaged O-ring, after reaming and chamfering)

### Activity Part 2: Watch the Pro Press Tool Video (10 minutes)

Video:

Have the class watch the video on how to use the RLS Pro Press tool (PPT slide #X)

- RLS Step-by-Step Demonstration

### Activity Part 3: Tube Preparation Practice (30 minutes)

Each installer completes the following:

- Utilize 4’ piece of pre-cut line set (3/8" and 3/4")

- Deburr inside and outside edges

- Clean outside of tubing near the fitting location until shiny

  - Scotchbrite

  - Spin around the tubing, do NOT run Scotchbrite vertically along tubing

- Mark fitting depth using fitting depth gauge

Instructor demonstrates common mistakes:

- Crooked cuts

- Missing depth mark

- Not deburring

- Damaging the O-rings

- Damaged/oval tubing

- Imperfections in tubing

- Pressing over manufacturer stamps in the tubing

### Activity Part 4: Press Connection Assembly (15 minutes)

Instructor-led demonstration:

- Put the appropriate size jaws on the tool (confirm the line set size)

- Perform a calibration cycle on the tool

- Insert while slowly spinning the tubing fully into fitting, to not damage the o-ring (confirm depth mark)

  - Note: it's not always possible to spin the line set into the fitting, do NOT force the tubing into the fitting, gently insert the tubing into the fitting.

- Open press jaws and seat them squarely over the fitting

- Confirm jaw alignment with press groove

- Activate tool and complete press cycle

- Visually inspect the press connection

- Use the crimp gauge to confirm proper press

  - Ensure the RLS logo has been stamped onto the fitting

- Repeat for:

- Straight coupling

- 90° elbow

Each installer completes the following:

- Properly insert tubing into fitting, spinning as to not damage the o-ring

- Tubing should be inserted to the proper depth mark

- Press jaws should be aligned and seated squarely over the fitting

- Activate the tool and complete press cycle

- Use the crimp gauge to confirm the press is correct

Checkpoint:

- Each installer must complete at least three successful presses

  - Straight coupling

  - 90° elbow

- Visually inspect the presses for proper connection, damage, etc.

### Activity Part 5: Real-World Scenario Challenge (20 minutes)

Scenario Example:

“Install a liquid line with two elbows and one service port connection inside a tight mechanical room.”

Constraints:

- Limited space

- One incorrect fitting intentionally mixed in

- Time limit

Installers must:

- Plan layout

- Choose correct fittings

- Execute clean presses

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Reasons a press fitting might leak

  - Damaged o-rings

  - Tubing not prepared properly

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Line Set Flaring using the NAVAC Tool

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

45–60 minutes

Group Size

Individual Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify the components of the NAVAC flaring tool

- Properly prepare copper tubing for flaring

- Create consistent flares using the NAVAC flaring tool

- Inspect flares for common defects

- Explain how proper flaring prevents refrigerant leaks

## Materials & Tools (per station)

- Systainer Kits - HOD-1, HID-3, HOD-TB

- NAVAC Line set Flaring Tool

- Pre-cut section of copper tubing (3/8" and 3/4")

  - 24 ⅝”

  - 18 ¼”

  - 12 ½”

- (6) ⅜” flare nuts

- (6) ¾” flare nuts

- Tubing cutter

- Oil

- Reaming/deburring tool

- Marker

- Safety glasses and gloves

### Safety Brief (10 minutes)

Instructor reviews:

- Wear eye protection when cutting and flaring copper

- Keep hands clear of rotating components

- Wear cut resistant gloves

- Ensure tubing is securely clamped before flaring

### Activity Part 1: Theory & Tool Overview (15 minutes)

Instructor explains:

- What is line set flaring

- Why we need to ream the line set before we flare

Instructor-led demonstration:

- Explain why the line sets need to be flared in order to properly seal on the flare blocks

- Identify NAVAC flaring tool components:

  - Quick-lock clamp block

  - Eccentric hardened steel cone

  - Size markings

- Explain importance of lubricating cone once a day

- Explain tool maintenance

  - Setup of brand new tool

  - Adjusting over time

### Activity Part 2: Watch the Flaring Tool Video (5 minutes)

Video:

Have the class watch the video on how to use the flaring tool (PPT slide #X)

- Perfect Flares Every Time w/ NAVAC NEF6LM

### Activity Part 3: Flaring with the NAVAC Flaring Tool (10 minutes)

Utilize the pre-cut section of line set: (12-1/2”, 18-1/4", 24-5/8")

Each Installer completes the following:

Prepare the Tubing

- Reem the inside of the line set where the flare is going to be made

- Sliding the flare nut onto the tubing (threaded side facing flare end)

- Marking tubing depth using the clamp guide

Insert the Tubing into the Flaring Tool

- Open the block and insert the tubing into the flaring tool block

- Set end of tubing flush with stop

- Clamp block down on tubing to ensure the correct depth of flare

- Push gauge away/back from tubing

- Insert block with gauge facing the tool until it clicks

  - allow the white marks to align with marks on steel plate

- Clamp down with the handle

Flaring the Tubing

- Push the power button and allow the machine to complete one full cycle until it stops

- Release the clamp

- Remove the block and unclamp from tubing with flare

- Check flare on gauge to ensure proper flare

- Check the inside of the flare for burrs and imperfections

- Repeat flaring on both ends of the 12-1/2” sections of line set

Checkpoint: Each installer must produce at least one flare in each tubing size provided.

### Activity Part 4: Inspection & Evaluation (5 minutes)

Installers visually inspect their flares:

- Smooth, even 45° angle

- No cracks or splits

- Flare centered and symmetrical

- No thinning at the flare edge/uniform edge all around

### Common Mistakes Discussion (5 minutes)

Group discussion:

- To avoid thinning the edges:

  - Do NOT reuse a flare after its been previously torqued

  - Make sure the tubing is inserted all the way into the stop gauge

- The effects of skipping deburring

- Crooked flares

  - Not having cone setting squarely in pipe

Instructor-led demonstration:

- A “bad flare” vs. a “good flare”

  - Pass around pre-made examples of bad flares to show the class what to look for

- Demonstrate the proper way to cut off a bad flare

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Attaching and Torquing Flare Nuts

Target Audience

Entry-level to intermediate Jetson installers

Duration

60 minutes

Group Size

Individual Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Explain what a service valve is

- Identify the different service valve sizes on a Jetson Air System

- Identify proper flare nut sizing and orientation

- Inspect flared tubing for defects

- Attach flare nuts correctly without cross-threading

- Apply proper tightening technique using two wrenches (including a torque wrench)

- Explain how improper flare connections cause leaks

- Explain why flare connections cannot be reused

## Materials & Tools (Per station)

- Systainer Kit - HOD-1 HID-3

- Precut Copper line set tubing (both 3/8" and 3/4")

  - 12 ½”

  - 18 ¼”

  - 24 ⅝”

- Flare nuts (correct sizes for each service valve)

- Flare fittings mounted on the training wall (male adapters or service valves)

- Adjustable wrenches

- Torque wrench

- Thread lubricant (e.g. Nylog)

- Oil lubricant

- Safety glasses and gloves

- Pre-flared tubing samples (pre-made good and bad examples)

## Safety Brief (5 minutes)

Instructor reviews:

- Eye protection required

- Sharp copper edges

- Proper wrench placement

- Proper back wrench technique

## Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor demonstrates:

- What a flare nut is

- Where on the Jetson Air System flare nuts are used

- What a service valve is

- What a torque wrench is

- How to set a torque wrench

  - in. lbs vs ft. lbs

- The purpose of using lubricant on the flare nuts

Installers demonstrate:

- Matching correct flare nut size to tubing size

- Installing flare nut onto tubing before flaring (discussion reminder)

- Identifying correct orientation:

  - Threads face outward

  - Tapered seat (threads) faces flared end of lineset

## Activity Part 2: Flare Inspection (5 minutes)

Each Installer completes the following:

- Inspect the provided flares and confirm each flare has:

  - Proper 45° flare angle

  - Smooth surface (no cracks, ridges, or splits)

  - Even flare thickness

  - Correct flare diameter

Hands-On Comparison:

- One good flare, properly seated

- Multiple defective flares (over-flared, under-flared, cracked)

## Activity Part 3: Attaching the Flare Nut (20 minutes)

Each Installer completes the following:

- Lightly oil flare face

- Align tubing squarely with male fitting

- Hand-tighten flare nut until fully seated

- Use two-wrench (backwrenching) method:

  - One wrench holds the fitting

  - Torque wrench tightens the flare nut

- Tighten to:

  - Manufacturer torque specs

    - 73 ft lbs for ¾ line

    - 26 ft lbs for ⅜ line

    - 50 ft lbs for ⅝” line

Instructor Coaching:

- Emphasize “hand-tight first” to prevent cross-threading

- Listen and feel for smooth tightening

- Emphasize the importance of proper torque:

  - Leaks

  - Proper seating of the flare

  - Not over-tightening

Instructor aks:

- “Using Notion, what size service valves does the 4 ton Jetson Air ODU have?”

- “What are the torque specs for those service valves?”

- “Why do we need to lubricate the flare nuts?”

## Assessment

Installers must demonstrate:

- Correct flare nut size selection

- Proper flare inspection

- Not cross-threading

- Back-wrench technique

- Correct torque technique

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Improper torquing

  - Over torquing

  - Under torquing

- Over-tightening causing cracked flares

- Dry flares causing binding against back of flare resulting in:

  - Incorrect torque

  - Twisting pipe

- Misalignment during tightening

- Cross-threading

- Reusing damaged flare nuts & flares

All of these can result in callbacks due to flare leaks

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Discussion: Removing Old Condensing Unit

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

3.5 hours

Group Size

2 - 4 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify the old equipment to remove

- Safely disconnect power and wiring from old equipment

- Safely reclaim refrigerant from old equipment

- Safely operate removal equipment and tools

- Remove and stage old equipment and materials

## Materials & Tools (per station)

- HOD-1 TB, HOD-3, HCOMM:0

- Refrigerant recovery machine

- Refrigerant scale

- Refrigerant recovery cylinder

- (2) - Dual VCRTs with sight glass

- Pressure probe

- (4) - ¼” x 48” refrigerant hoses

- Nutdrivers (¼”, 5/16”)

- Electrical tape

- Non-contact voltage tester

- Safety glasses & gloves

### Safety Brief (5 minutes)

Instructor reviews:

- Power to the unit must be disconnected

- TARE weight of cylinders

- Maximum pressure of cylinders

- Maximum capacity of recovery cylinder 80% of total capacity

- Never mix different types of refrigerants

- Skin exposed to refrigerants can cause serious injuries

- Work in well ventilated areas

- Always wear proper PPE

### Activity Part 1: Theory & Tool Overview (20 minutes)

Instructor explains:

- Why it's important to follow specific steps to complete this process

- Being meticulous and efficient when removing the old system

- How communication and coordination between IDU & ODU installers creates efficiency

Instructor-led Explanation:

The instructor should bring the installers over to the old demo ODU and explain all of the steps taken to remove the unit.

- At the old ODU demo unit, identify the following:

  - Nomenclature/rating plate

  - How many (approx) pounds of refrigerant will be removed from the old system

  - Planning the route to take the old unit out to the staging area for disposal

  - Tools to perform removal

  - Planning and staging the new equipment and necessary tool to install the 
new equipment

### Activity Part 2: Disconnect Old ODU Electrical Connections (20 minutes)

Instructor explains:

- Start by disconnecting all electricity from the unit

- Shut off power to the ODU at the disconnect (pull vs blade switch type)

- Shut off power to the circuit breaker marked “A/C” in the main electrical panel

  - Don't assume the circuit is marked correctly!

- Remove the electrical control box cover on the old outdoor unit

- Use a non-contact voltage tester to confirm an absence of power

- Cut the electrical whip as close to the outdoor unit as possible

- Cut communication wire as close to the outdoor unit as possible

### Activity Part 3: Pre-Removal of Refrigerant from Old Unit  (20 minutes)

Instructor-led demonstration:

- Visually inspect the recovery cylinder for physical damage, rust, or anything that could weaken the structure

- Recovery cylinders are dedicated to the specific type of refrigerant being recovered and must be properly marked

  - Do NOT mix refrigerant types in the same cylinder

Understanding Recovery Cylinder Stamps On Handle

- Max Pressure - (e.g. DOT- 4BA400) indicating 400 psi

- Manufacture Date: Do NOT use if over 5 years

- Water Capacity (WC) Is the pounds in water to fill the cylinder stamped on it 100%

- Tare Weight (TW) of the cylinder when empty

SAFETY NOTE:

- Recovery cylinders should never be filled more than 80% of the total cylinder volume

- Recovery cylinders should never be left digging in the sun

### Activity Part 4: Removal of Refrigerant from Old Unit  (30 minutes)

Instructor-led demonstration:

Demonstrate the steps below to remove refrigerant from the old unit:

Prepare Service Valves for Recovery:

- Remove the ⅜” and ¾” service valve stem caps

- Remove the ¼” Schrader cap covers

- Verify that all valves are fully back seated (completely open) by checking that the Allen wrench opening is at the port closest to the cap end

- Attach the Schrader valve core stem removal tools (VCRT) to the liquid line and suction line valves

- Remove the Schrader valve core stems from both valves

  - Shut-off both valves

  - Remove the Schrader core removal section from the VCRT and set aside for reassembly later

Prepare Recovery Cylinder

- Set up weigh scale on firm level ground and turn it on

- Set the recovery cylinder on the weigh scale

  - Keep the max weight and pressure in mind while recovering refrigerant

Make Recovery Cylinder Connections

- Connect the RED hose between high-side ( ⅜”) service port of condenser and the run end of ¼” flare T

- Connect the BLUE hose between low-side (¾”) service port of condenser and the branch of ¼” flare T

- Connect the YELLOW hose between the open end of the T to the filter drier (attached to the recovery machine inlet.)

  - Run = straight-through/horizontal section of the tee

  - Branch = the vertical section of the tee

- Attach the 2nd YELLOW hose between the outlet of the recovery machine and the Vapor Port (BLUE valve) on the recovery tank

Position Valves and System Setup

- Make sure all valves are in the closed position (vacuum machine and service valves)

- Turn the low side and high side VCRT valves to the open position

- With the recovery machine dial in the closed position, slightly throttle up the dial on the recovery machine

Air Purging & Cylinder Handling

- Slightly crack open the ¼” hose connection at the recovery cylinder to remove air trapped in hoses for 10 - 15 seconds until all air is removed and refrigerant fills the lines.

- Tighten the ¼” hose fitting

- Open the BLUE recovery cylinder valve

Recovery Operation

- Turn the recovery machine to ON

- Slowly turn up the recovery machine dial from slightly open to fully open

- Listen for “liquid slugging”. If “liquid slugging” occurs:

  - throttle machine down

  - Target 50 psi inlet pressure on the machine readout

  - Keep throttling the control knob on the recovery machine for 5 - 10 minutes until the machine is able to run without slugging

- The recovery machine will run until it automatically shuts off

- After auto shut-off, press START once more and let the system run and auto shut-off a second time.

- After recovery is complete, set the dial to CLOSED.

Post-recovery & Self-purge

- Press START on the recovery machine

- Slowly rotate the knob to SELF PURGE to empty the recovery machine into the recovery cylinder without any sudden changes in pressure

- Let the recovery machine complete the cycle and it will automatically shut-off

- After purge is complete, set the dial to CLOSED

Shutdown & Disconnect

- Close the BLUE vapor valve on recovery cylinder

- Disconnect hoses + VCRTs

  - Be careful with the outlet hose of the recovery machine connected to the BLUE vapor valve, it will have residual refrigerant in it

  - Crack it slightly and let it evaporate

- Cut old suction line and liquid lines

- Crimp the old lines connected to the unit and seal with electrical tape to prevent oil leakage

- Seal old line set with electrical tape (if re-using).

- Move the old unit to the staging area

### Activity Part 5: Guided Practice Refrigerant Recovery from Old Outdoor Unit (60 minutes)

Instructor explains:

- Each installer completes a refrigerant recovery on an old outdoor unit

- Pull up the SOP from Notion on your phone and follow the instructions

- Instructor will circulate, observe and answer questions

Checkpoint: Each group must complete at least one recovery process.

### Activity Part 6: Old Equipment Removal and Jobsite Cleanup (5 minutes)

Instructor explains:

### At this point:

### The electrical connections have been cut from the old ODU

### The old refrigerant has been completely recovered

The final steps to removing the old ODU are:

- Cut the old suction and liquid lines cleanly from the unit

- Crimps old lines at the unit

- Seal old line set with electrical tape to prevent oil leakage

- Use a dolly to safely move the old unit to the staging area

### Activity Part 7: Q&A (15 minutes)

Instructor asks:

- Why do we remove the Schrader cores before starting refrigerant recovery?

  - What problems can occur if we don’t remove them?

- What safety or accuracy issues can happen if the scale is not on level/stable ground?

- How do you determine whether the recovery cylinder can safely accept the refrigerant being removed (weight and pressure limits)?

- Explain the purpose of the ¼” × ¼” × ¼” tee in this setup and what would happen if it were installed incorrectly.

- What is the purpose of purging air from the hoses before opening the recovery cylinder vapor valve?

  - What risks does air introduce into the system?

- What does reaching 0 pressure indicate during the recovery process?

  - Why is auto shut-off important?

- Why is the self-purge step necessary?

  - What refrigerant remains if this step is skipped?

- After recovery is complete, why must the suction and liquid lines be crimped and sealed before moving the old unit?

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Not removing Schrader valves

- Not correctly weighing the cylinder

- Not purging the hoses of air before beginning the recovery process

- Not crimping the line of the old unit before moving it to the staging area

## Clean up (15 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

### Extra Activity: Watch the Refrigerant Recovery Video (25 minutes)

Video:

Assign this video as extra work for people who are struggling with recovery. (start - 26:35)

- https://www.youtube.com/watch?v=NhD6ipF5NKY

## *Instructor Note*

- On the last day of class, have the installers re-charge these old units with old refrigerant to prepare/charge the old ODUs for the next class.

## Discussion: Removing Old Forced Air Unit

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

2 hours

Group Size

2 - 4 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify the old equipment to remove

- Safely disconnect and cap off gas supply line

- Safely disconnect and cap off the exhaust flue

- Safely disconnect electrical power and wiring

- Safely disconnect and remove condensate system

- Safely disconnect supply and return plenums

- Safely operate removal equipment and tools

- Remove and stage old equipment and materials

## Materials & Tools (per station)

- HID-1 TB, HID-1, HID-2, PT-1

- ½” gas line cap

- 4” flue vent plug

- Tubing cutter

- Pipe wrench

- Screwdriver

- Wire stripper

- Electrical tape

- Non-contact voltage tester

- Safety glasses & gloves

### Safety Brief (5 minutes)

Instructor reviews:

- Ensure that electrical power to the unit is OFF

- Ensure gas supply at the meter is OFF

- Use a back wrench when removing a gas line

- Turning gas meter back on safely

- Test all new/replaced gas fittings and surrounding connections (soap test)

- Ensure the old flue pipe is capped to prevent carbon monoxide intrusion

- Testing all gas appliances for proper operation (including pilot lights)

- Wearing proper PPE

### Activity Part 1: Theory & Tool Overview (15 minutes)

Instructor explains:

- Why it's important to follow specific steps to complete this process

- Being meticulous and efficient when removing the old system

- Why communication and coordination between IDU & ODU installers creates efficiency

- Eliminate any potential damages to customers property or system being connected too.

Instructor-led demonstration:

- Identify the parts of the existing system:

  - Furnace

  - Condensate pump and piping

  - A/C Coil

  - Gas pipe

  - Flue Pipe (various sizes)

  - Power supply & wiring

  - Blower assembly

  - Supply & return plenums

  - Boilers

    - What they are

  - Electrostatic air cleaners:

    - What they are

    - What to do if the homeowner wants to keep it

### Activity Part 2: Disconnect Old IDU Service Connections (20 minutes)

Instructor explains:

“It’s important to think ahead when you start removing the old equipment from a customer’s home. Much of this equipment will be removed, but things like the plenums will be reused, so it’s important to take that into consideration before you start cutting everything.”

- Start by disconnecting all electricity from the unit

- Use a non-contact voltage tester to confirm an absence of power

- Shut-off gas at the gas meter

- Disconnect the gas line from the old unit

- Cap remaining gas line with gas line cap

- Disconnect the flue pipe

- Cap remaining flue pipe to prevent carbon monoxide intrusion

- Remove the condensate pump

- Disconnect the coil and seal with electrical tape to prevent oil leakage

- Disconnect the supply and return plenums

  - Remove the old tape or sealant

  - Remove the old zip screws

- Prepare plenums for new transitions to new equipment

  - NOTE: Need to know the total height of the new IDU and know how much of the existing supply plenum to cut (approx. 4-12" above the old furnace)

- Move the old unit to the staging area

- STOP: Do NOT continue installation until:

  - Electricity is turned back ON

  - Gas is turned back ON

  - Gas connection (cap) is soap tested

  - Pilot lights are ON and gas appliances are operational

  - Flue pipe is capped

### Activity Part 3: Q&A Process and Safety Understanding (30 minutes)

Instructor asks:

- What should you do before disconnecting the lines set to the A/C coil?

- What should you do after disconnecting the lines set to the A/C coil?

- What should you do before removing the condensate pump?

- What should you do once you've capped off the gas line?

- What safety precautions should you perform before removing the unit?

- What are some considerations for reusing the existing supply plenum?

- Why is it important to cap off the old furnace flue pipe?

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Taking too long to remove the old unit

- Cutting the old unit into multiple pieces

  - Wasting too much time getting it out of the way

- Forgetting to cap the gas line

- Forgetting to turn the gas back on

- Not soap testing the cap on the gas line

- Not checking pilot lights and gas appliances

  - Call backs because the customer isn’t able to turn the gas stove or dryer on

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Building Supply Plenum Transitions

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

3 - 4 hours

Group Size

Individual Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Accurately measure an air handler outlet

- Design a proper plenum transition

- Fabricate a plenum transitions using sheet metal

- Properly assemble and seal plenums

- Explain how transition design affects airflow and noise

## Materials & Tools (per station)

- Mock air handler wall

- HID- 1, PT-1, PS

- (1) - Temperature/Humidity Sensor

- (2) - 2’ x 4’ pieces of 28 gauge sheet metal

- (2) - 60” S-cleats

- Sheet metal tools:

  - Snips

  - Folding bar

  - Tongs

  - Cross Break Tool

- Tape measure

- Impact drill

- Self-tapping sheet metal screws

- Foil tape

- Folded up trash container

- Safety glasses and gloves

## Safety Brief

Instructor reviews:

- Sheet metal is extremely sharp!

- Importance of cleaning up the small pieces of snipped metal

  - People and pets can step on them

  - They get caught on shoes and can scratch floors

- ALWAYS wear gloves and glasses when doing this work

## Setup (Instructor Prep)

- Each station gets:

  - (2) 2’ x 4’ pieces of 28 gauge sheet metal

  - (2) - 60” S-Cleats

- Self-tapping sheet metal screws

- Foil Tape

### Activity Part 1: Theory & Tool Overview (10 minutes)

Start this activity at the complete Jetson Air System in the classroom so that installers can see a fully installed plenum transition.

Instructor explains:

- What the plenum transition is

- When is it necessary to build a new transition on-site

- Foil tape and the importance of proper sealing

- Cross-breaks and the reasons for adding them to the sheet metal

Move the group over the mock transition wall to discuss the tools and materials.

Instructor-led demonstration:

- Provide a brief explanation and demonstration of each of the tools

- Provide a brief  explanation of the materials

### Activity Part 2: Instructor Builds a Supply Plenum Transition (45 minutes)

Instructor-led demonstration:

- Use one of the transition stations to build a supply transition

- Provide guided instruction for each step in the process

- Explain how to properly measure each side of the transition

- Explain how to safely and properly cut each piece of metal

- Emphasis should put on safety (cut resistant gloves and glasses)

- Explain proper sheet metal bending technique

- Explain why you have to pre-plan which pieces get screws

- Explain the reason for making cross-breaks in the transition pieces

- Show the proper method for making cross-breaks

Instructor note:

- Remove the example transition after the demo to allow room for four  installers to practice

### Activity Part 3: Guided Practice Building Transitions (90 minutes)

Each installer completes the following:

- Starting with the rear section, measure the height and width of first piece of sheet metal

- Cut the rear section according to the measurements

- Cut V’s in corner to allow lips to bend

- Make the cross-break in the rear section

- Bend the edges to make the lips

- Fit and secure the rear section onto the plenum

- Continue making each section of the plenum transition

- Properly secure the sections in the s-cleats

- Properly secure the sections with zip screws

- Properly tape all seams with foil tape

Instructor circulates to ensure the following:

- Correct tool usage (e.g., using snips)

- Taking proper measurements (ability to read a tape measure)

- V’s notched correctly in corners

- Making proper 1 inch bends/lips on the edges

- Making proper cross-breaks

- Installing screws

  - Proper locations

  - Proper quantity

  - Missing screws?

- Joints sealed tightly

- Installing foil tape with minimal creases

- Aesthetics

- Clean work area

- Safety!

Checkpoint:

- Each installer must complete at least three transitions

- Track the time it takes the installers to build each of the transitions to show their skill progression

### Activity Part 4: Real-World Transition Challenges (90 minutes)

This can be done if time allows and the installers are ready, or this can be revisited later to provide additional real-world practice.

Challenge #1 - Plenum Offset

- On the mock wall, slide the transition tops over so that the installers need to create a transition at an angle.

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- What happens when you don’t notch V’s in the corners?

- What happens when you don’t seal with foil tape?

- What happens when you don’t add cross-breaks?

## Debrief & Key Takeaways

Group discussion:

- What issues caused you to make mistakes?

- What did you find most difficult?

- What got easier the more times you practiced it?

- The importance of making the plenum transitions look good

- When we need to add insulation

- What if the customer wants to re-use an electrostatic air cleaner?

### Extra Activity: Watch the Transition Building Video (35 minutes)

Video:

Assign this video as extra work for people who are struggling with building transitions.

- Strobel_Transition.MOV

## *Instructor Note*

- The following activity will be installing the basecan

- This activity transitions directly into the next

- Installers should clean up any scrap/trash in their work area to maintain a clean job site

- Installers should not put away any necessary tools needed to assemble the base can

- The final transitions (return and supply) that the installers build will need to be left intact until after the Installing Sensors Hands-on Activity

## Hands-On Activity: Assembling and Attaching the Return Air Base Can for IDU

Target Audience

Entry-level to intermediate Jetson installers

Duration

2.5 hours

Group Size

Individual Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Explain the purpose of an air handler base can

- Correctly measure the base can size for an air handler

- Fabricate a square, level, and airtight base can

- Seal and prep the base can for field installation

## Materials & Tools (per station)

- Systainer Kit - HID- TB, HID -1,2,3

- (1) - 21 x 22 Base can (Part Number HVBAS-07)

- (2) - 60” S-cleats

- (1) - 2’ x 4’ 28 gauge sheet metal

- Self-tapping sheet metal screws

- Foil tape

- Foam tape

- Tape measure

- Level

- Snips

- Hand brake or folding bar

- Drill/impact

- Marker

- Safety glasses and gloves

## Safety Brief

Instructor reviews:

- Sheet metal is extremely sharp!

- Importance of cleaning up the small pieces of snipped metal

  - People and pets can step on them

  - They get caught on shoes and can scratch floors

- ALWAYS wear gloves and glasses when doing this work

## Activity Part 1: Theory & Tool Overview (15 minutes)

Instructor explains:

- “For this activity, you are installing a vertical air handler in a closet. The unit requires a prefabricated base can to support the unit and allow for return airflow.

- Why base cans are necessary for the installation of the IDU

- Difference between:

- Structural support

- Airflow management

- Filter access

- Why foam tape between IDU and base can is necessary

- Common failures:

  - Air leaks

  - Out-of-square

  - Incorrect height

## Activity Part 2: Measurement & Planning (15 minutes)

Instructor-led demonstration:

- Measure air handler footprint (height and width)

- Determine:

  - Base can height

  - Return opening size and location

  - Filter slot position (front)

Instructor Checkpoint

- Measurements recorded correctly (measure twice cut once!)

- Allowance for seams and cleats

Instructor asks:

- Are return ducts as important as supply air ducts?

- Are air leaks in the return a big concern?

- Why are smooth transitions important?

- What would you consider the most important part of installing the return air can?

- When assembling the return air can on a 2 ton unit, do you need to install the support brackets?

- Why is the foam tape so important?

### Activity Part 2: Watch the Instructor Assemble Base Can (15 minutes)

Instructor-led demonstration:

- The instructor assembles a base can while explaining the process to the class

- Provide guided instruction for each step in the process

- Explain how to take proper measurements

- Explain how to safely and properly cut each piece of metal

- Emphasis should put on safety (cut resistant gloves and glasses)

## Activity Part 3: Guided Practice Assembling the Base Can (60 minutes)

Each installer completes the following:

- Lay out base panels:

  - Front

  - Back

  - (2) - Sides

  - Bottom flange (if required)

- Cut and bend metal

  - Opening size for the 3 Ton unit:

    - 20.8" deep  x 16.3 width

- Form corners and seams

Instructor circulates to ensure the following:

- Correct tool usage (e.g., using snips)

- Taking proper measurements (ability to read a tape measure)

- Making proper 1 inch bends/lips on the edges

- Making proper cross-breaks

- Square layout

- Clean bends

- Consistent seam allowances

- Installing screws

  - Locations

  - Quantity

- Installing foil tape

- Structural rigidity

- Safety

Checkpoint:

- Each installer must complete at least 2 base can assemblies

- Track the time it takes the installers to build each of the transitions to show their skill progression

## Activity Part 4: Guided Practice Mock Installation and Sealing (30 minutes)

Each installer completes the following:

- Place air handler on top of base can to verify:

  - Proper fit

  - Level condition

  - Full contact support

  - Filter slot cover hangs over the base can ¼”

- Seal all interior seams with foil tape

- Tape exterior seams to the side of the return plenum

Instructor circulates to ensure the following:

- Base can level from to back and left to right

- Foam tape required between base can and IDU

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Unlevel base can

- Unsquare base can

- Common failures:

  - Air leaks

  - Out-of-square

  - Incorrect height

- Not leaving enough room to remove the filter

## Debrief & Key Takeaways (10 minutes)

Group discussion:

- How the base can affects system airflow and serviceability.

- What happens if the base can be out-of-square?

- What happens if the base can have leaky seams?

- What happens if the floor under the base can is unlevel?

- What is a downflow base?

## Transition to the Installing Sensors Hands-on Activity

Instructor note:

- This activity transitions directly into the next

- Installers should clean up any scrap/trash in their work area to maintain a clean job site

- Installers should not put away any necessary tools needed to install the sensors

- The final transitions (return and supply) that the installers build will need to be left intact until after the Installing Sensors Hands-on Activity

## Hands-On Activity: Installing Sensors - Mounting

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

2.5 hours

Group Size

Individual Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify proper sensor placement on a supply plenum

- Properly install the temperature & humidity sensor

- Properly install the air quality (IAQ) sensor

## Materials & Tools (per station)

- Systainer Kits ESEN

- (8) - Temperature & Humidity Sensor

- (8) - Indoor Air Quality Sensor

- Impact + step bit (Temp/Hum sensor)

- 2.5” hole saw (IAQ sensor)

- Self-tapping sheet metal screws

- Impact + bits

- Screwdriver

- Wire ties

- Safety glasses and gloves

### Safety Brief (5 minutes)

Instructor reviews:

- Sharp metal edges

- Eye protection when drilling into metal

- Cleaning up metal shavings from work area

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor-led demonstration:

- Gather the class around the classroom demo system to show where the sensors are installed on the system

- Have loose sensors to pass around while explaining each of them

Instructor explains:

- The purpose of each sensor:

  - Temperature & humidity and IAQ sensor

    - What each of the sensors measure

    - Why they’re necessary for system operation

    - Why placement of the sensors matters

    - Why proper installation is critical:

      - Direction of probe affects the reading

- How they terminate at the Jetson Hub

  - Provide a brief explanation (wiring will be covered in another section)

### Activity Part 2: Installing the Temperature & Humidity Sensor (30 minutes)

Instructor-led demonstration:

- Choose correct plenum

  - Supply air

  - Explain why location matters

- Mark the location on the supply plenum

  - 12 - 24 inches downstream of airflow mixing

  - Centered on plenum face when possible

- Drill the opening

  - Use the impact with a step bit to drill a hole for sensor probe

  - Be mindful of shavings falling into plenum

- Insert sensor

  - Remove sensor protective cover

  - Probe fully in airflow (not touching metal)

- Secure sensor

  - Remove white cover plate with screw driver

  - Use 2 screws to secure in provided holes

  - Ensure firm, vibration-free mount

Quality Criteria:

- Proper orientation

- Tight seal

### Activity Part 3: Installing the Air Quality Sensor (30 minutes)

Instructor-led demonstration:

- Choose correct plenum

  - Return air

  - Explain why location matters

- Mark the location

  - Away from turbulent areas inside the plenum

  - Centered if possible

  - 2’ away from any turns

- Drill the opening

  - Use 2 ½” holesaw

  - Clean sharp edges

- Install sensor

  - NOTE: double check that black sensor tip has not fallen off

  - Correct airflow orientation

    - Vanes aligned parallel in the airflow

Quality Criteria:

- Proper orientation

- Tight seal

### Activity Part 4: Guided Practice Installing Both Sensors (60 minutes)

Each installer completes the following:

- Install the Temperature & Humidity Sensor

  - Choose correct plenum

  - Mark the location

  - Drill the opening

  - Insert sensor

  - Secure sensor

- Install the Air Quality sensor

  - Choose correct plenum

  - Mark the location

  - Drill the opening

  - Install sensor

Instructor circulates to ensure the following:

- Correct plenum location

- Correct and safe tool usage

- Sensors oriented correctly

- Installing screws to secure the sensors

- Safety!

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Putting the sensors on the wrong plenum

- Putting the sensors too close to a bend or turbulent air

- Incorrect orientation of the sensor inside the plenum

- Losing the black plastic tip on the IAQ sensor

## Debrief & Key Takeaways

Group discussion:

- Why is correct placement of the sensors important?

- Why is proper sealing around the sensors important?

- How does bad sensor placement affect comfort and system performance?

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Installing a Condensate Pump

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

90 minutes

Group Size

2 - 4 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Identify when a condensate pump is required

- Correctly mount and plumb a condensate pump

- Make wire connections between the pump switch, overflow switch, and theIDU

- Test pump operation

- Diagnose common installation errors

## Materials & Tools (per station)

- (1) - Damaged IDU

- (1) - Condensate pump - PS

- (1) - Condensate pan overflow switch - HID- 2

- 5’ - ⅜” Vinyl tubing (5’) - PS

- PVC pipe & fittings - HID-2

  - 5’ - ¾” PVC pipe - PS

  - (2) - ¾” MIPs

  - (1) - plug

  - (5) - 90s

  - (1) - trap

  - (1) - tee

  - (1) - socket union

- (2) - teflon tape

- (1) - can of PVC primer and glue

- (1) - can of PVC glue

- Drill & bits HID - TB

- PVC ratchet cutter - HID-TB

- Level

- Screwdriver

- Wire strippers

- (6) - Blue wire nuts

- Zip ties

- 5 gallon bucket

- Safety gloves and glasses

### Safety Brief

Instructor reviews:

- Power must be OFF before performing electrical work!

- Never route discharge tubing where freezing can occur

- Wearing proper PPE

- Skin contact with chemicals (primer and glue)

### Activity Part 1: Theory & Tool Overview (5 minutes)

Instructor explains:

- The purpose of a condensate pump on a Jetson Air System

- When a condensate pump is needed vs. when not needed

  - If floor drain exists

Instructor-led demonstration:

- Identify parts of the condensate pump:

  - Pump (110 volt)

  - Internal float switch (inside pump, normally closed)

  - Condensate pan overflow switch

  - PVC pipe

  - Vinyl tubing

  - Fittings

### Activity Part 2: Determine Pump Requirement & Location (10 minutes)

Instructor-led demonstration:

- Inspect IDU location and determine drainage destination

- Prioritize gravity drain line if possible

- Select a pump location:

  - Level

  - Accessible for service

  - Away from filter access cover

  - Below drain outlet on the IDU

  - Near a power source

### Activity Part 3: Secure and Level the Pump (5 minutes)

Instructor-led demonstration:

- Place pump on a vibration-resistant surface

- Level the pump (critical for float operation)

- Securely mount the pump lower than the IDU drain outlets

  - Depending on the level of the IDU drain outlet:

    - Side of unit

    - Floor

    - Ground

### Activity Part 4: Install Condensate Drain Line to Pump Inlet (5 minutes)

Instructor-led demonstration:

- Install trap and union

  - Grade pipe downward to pump

  - Ensure support under piping and fittings

- Cut PVC cleanly and insert to pump inlet

- Avoid installing the pump/PVC in a location that blocks the IDU filter slot

- Install overflow switch in overflow port of the IDU

Instructor explains:

How improper support and slope causes water backup and overflow faults.

### Activity Part 5: Install Discharge Tubing (10 minutes)

Instructor-led demonstration:

- Connect discharge tubing to pump outlet

- Route tubing:

  - Upward - only to rated lift height on pump specs sheet

  - Slope continuously to termination

- Secure tubing every 3 – 4 feet

  - To the lineset

  - To the truss/joist

- Terminate per local code to appropriate discharge locations:

  - Outside by the ODU

  - Laundry drain

  - NOT above walkways

  - Not on to sidewalks

Instructor explains:

- How excessive lift or long horizontal runs cause strain on the pump which causes potential for premature pump failure.

- The best way to install a condensate drain is to floor drain or outside, this removes another potential mechanical failure.

### Activity Part 6: Wire the Overflow Switch (10 minutes)

Instructor-led demonstration:

- Identify the condensate pan overflow switch leads

- Identify the condensate pump overflow switch leads

- Wire in series:

  - Condensate pan overflow switch

  - Condensate pump

- Connect to the CN5 connection on the IDU control board:

  - CN5 has a blue jumper wire

  - Cut blue jumper wire.

  - Connect one blue lead to one lead of the overflow switch.

  - Connect the other overflow switch to one pump wire.

  - Connect the remaining pump wire to the other blue lead at CN5

- Manage all wires neatly

Instructor asks:

- “What happens electrically when the pump overflows?”

### Activity Part 7: Power & Functional Testing (5 minutes)

Instructor-led demonstration:

- Plug the condensate pump into an extension cord to test

- Slowly pour water into the p-trap until it triggers the condensate pump.

- Verify:

  - Pump activates

  - Water discharges properly

  - Safety switch shuts system off when float is lifted

  - Wire is removed from safety switch

### Activity Part 8: Guided Practice Condensate Pump Installation (30 minutes)

Each installer completes the following:

- Determine pump location on the IDU

- Secure and level the pump

- Install overflow switch

- Install trap and drain line to pump from the IDU

- Install support of drain (if needed)

- Install discharge tubing

- Properly wire the overflow switch and condensate pump

- Power on and functional test the pump

Instructor circulates: Ensure groups are installing pipes/tubing correctly and making proper wire connections.

Checkpoint: Each group must complete at least one condensate pump installation.

### Activity Part 9: Troubleshooting Q&A (5 minutes)

Instructor asks:

- What should you do if a condensate pump runs continuously?

- What should you do if a pump does not turn on?

- What should you do if water is backing up into the pan?

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Not priming the condensate pump

- Not priming the trap

- Not wiring the overflow switches

  - Could flood the basement!

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Assembling the ODU Stand and Bracing the ODU to a Wall

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

3.5 hours

Group Size

2 Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Demonstrate preparing a level gravel base

- Identify the location and necessary preparation ODU stand paver base

- Identify all components of the ODU base stand

- Level and secure the stand for outdoor installation

- Mount the ODU on the base stand

- Secure the ODU to the wall using aircraft cable

- Explain the reason for attaching aircraft cable

- Demonstrate the installation of aircraft cable

## Materials & Tools (per station)

- Systainer Kit - HOD-2, HOD-TB

- ODU base stand kit - PS

- Paver Base

- (4) - Bags of ¾” gravel base rock - PS 1

- (2) - Bags of ¼” gravel - PS-2

- Shovel

- Tamper

- Pick Axe - VF

- (1) - ODU

- Base Pad Trainer

- 3 - 4 Buckets

- Sieve

- Metric Socket Set or ¼” bit attachments

- Impact drill

- Level

- ODU stand installation manual

- 16” aircraft cable

- (2) - ¼” X 1-½” lag bolts and washers

- (2) - 3/16” X 1-¼” Tapcon concrete screws and washers

- Knee pads

- Safety glasses and gloves

## Setup (Instructor Prep)

- Utilize the Base Pad Trainer to discuss proper gravel placement

- Provide an unassembled ODU stand to the group

  - New stand in the box or re-used training stand

  - Have installers keep the box intact to reuse for future labs

- Provide the group with the ODU installation manual

### Activity Part 1: Theory & Tool Overview (20 minutes)

Start this activity at the complete Jetson Air System in the classroom so that installers can see an assembled ODU base stand.

Instructor explains:

- Purpose of the stand

- When is it necessary to install a stand vs. when the ODU can sit directly on the base pad

  - Snow

  - Take into consideration exhaust and air intake

  - Consider electrical, lineset and line hide while positioning pad, stand, unit, and wall anchors

- Importance of prepping and leveling the ground under the base pad with gravel

- Importance of leveling the base pad

- Importance of squaring and leveling the ODU stand

- ODU must be positioned 12” from the wall (clearances)

- The stand should be placed symmetrically on the pad - Aesthetics!

- Importance of securing the ODU to the wall using aircraft cable

### Activity Part 2: Prepping the ODU Base (60 minutes)

Instructor explains:

- Why it’s necessary to lay down a level gravel base before setting the base pad down

  - Unlevel pad can create vibration, noise, and equipment stress

  - This will ultimately lead to system failure

- If necessary, clear the area where the base will be installed.

- If plants need to be removed, ask the owner if they would like them saved and where you can put them in a safe place where they won’t get damaged

- Dig down to an even depth below the topsoil

- Add the 4 bags of ¾ gravel, 1 at a time and tamp out until even and level in all directions

- Add the remaining 2 bags of ¼ gravel, 1 bag at a time and tamp out until even and level in all directions.

- Use level to confirm

- Discuss the importance of planning ahead:

  - Where is all of the equipment going to be installed?

  - Where are the linesets coming from?

  - How far away from the house does the ODU need to be?

  - Making sure everything is square, level and even so that it looks good once it's all installed

  - All of this determines where you start to dig and where the gravel goes

Each group of two completes the following:

- Pour 4 bags of ¾ gravel, 1 at a time and tamp out until even and level in all directions

- Pour 2 bags of ¼ gravel, 1 bag at a time and tamp out until even and level in all directions

- Place ODU stand pad on the gravel and ensure the pad sits level on the gravel

Instructor circulates to ensure the following:

- Correct tool usage

- Correct usage of gravel

- Confirmation that the gravel is level

- Final confirmation that the pad sits level on the gravel base

### Activity Part 3: Guided Practice Assembling the ODU Stand (60 minutes)

Instructor explains:

- Now that the pad is level, it's time to assemble the stand.

- The stands are one size fits all, however, they need to be adjusted for the various size ODUs that we install

- Provide the following measurements:

  - 2-Ton ODU units - 26.1 Inches

  - 3-Ton ODU units - 23.0 Inches

  - 4 & 5 Ton ODU units - 23.6 Inches

Each group of two installers completes the following:

- Unbox the ODU stand

- Utilize the instructions to assemble to ODU stand

Instructor circulates to ensure the following:

- Correct tool usage

- Stability of the stand

- Correct orientation of the stand parts

- Stands are assembled to the correct dimensions of the unit

- Safety

Checkpoint:

- Each team must assemble the base stand at least 2 times

- Track the time it takes the installers to assemble the stand to show their skill progression.

- If time allows, assemble the stand a third time. Make it a competition with every team starting at the same time and see how can complete the assembly the fastest.

### Activity Part 4: Placing and Securing the ODU to the Stand (45 minutes)

Each group of two installers completes the following:

- Place the assembled stand on the base pad

- Place a training ODU on the stand

- Secure the ODU to the stand and ensure that it’s level

- Attach aircraft cable (seismic bracing) to the ODU

- Attach the other end of the aircraft cable (seismic bracing) to location to wall

Instructor circulates to ensure the following:

- Correct tool usage

- Stand is level

- Stand is placed 12” from the wall

- The ODU feet are aligned with the pad and the wall of the house (aesthetics)

- The aircraft wires, concrete anchors/lag bolts, and washers secured

- Safety (lifting)

Checkpoint:

- Each installer group must secure the ODU to the stand and secure to the training wall at least  once

- Instructor to confirm that the unit is securely and correctly fastened to the wall

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Not attaching aircraft cable

  - What is the danger in not securing the unit with aircraft cable?

- Base pad not perfectly level

- Not installing an ODU stand in an area that requires the ODU to be mounted on a stand.

  - In what circumstances is it necessary and when is it not necessary to install an ODU stand?

- Not centering the ODU on the pad

  - Aesthetics!

- Not installing the ODU far enough away from the side of the house.

  - How far from the house do we mount the ODU on the stand? Why?

## Clean up (15 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble ODU from stand, stand and put back in the box.

- Clean up work area of debris and scrap material

- Remove and sort gravel from the gravel base boxes

  - Shovel gravel through the screen/mesh into the buckets

  - Separate the ¾” and ¼” gravel into separate buckets

## Hands-On Activity: Line Set Cleaning Using Solvent and the Hilmor Line Set Cleaner

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

90 minutes

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Explain why line set cleanliness is critical to system reliability

- Identify components of the Hilmor Line Set Cleaner kit

- Properly clean a refrigerant line set using the Rx11 and the Hilmor Pig tool

- Evaluate line set cleanliness after flushing

- Describe potential system failures caused by contaminated lines

## Lab Board: Line Set Cleaning

Tools (per station)

- Systainer Kits: HOD-2, HOD-3

- Hilmor Line Set Cleaner tool

- Nitrogen cylinder and regulator

- Collection buckets, rags and mesh bag

## Materials (per station)

- (1) - ⅜” and ¾” Cleaning Pigs (Hilmor pigs as specified)

- Rx11 cleaning solvent

### Safety Brief (5 minutes)

Instructor reviews:

- Review hazards of working with solvent and cleaning chemicals

- Only use the Rx11 flush system with the equipment that came with the kit

- Projectile pigs can cause injuries

- Wear required PPE: minimum gloves and glasses

- Ensure proper ventilation when handling solvents

- Collect and dispose of solvent and waste pigs per environmental plan

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- Why line sets must be cleaned

- Common contaminants:

  - Oil residue

  - Moisture

  - Carbon residue (from old/poor brazing)

- We clean lines from inside of the house towards the outside of the house

  - Avoid blowing solvent/contaminants into the home

  - Use 50’ hose for attics to avoid carrying nitrogen cylinders into the attic

Instructor-led demonstration:

- Instructor identifies the Hilmor Line Set Cleaner components:

  - Injection/connection point

  - Directional flow design

  - Rx11 Flush valve off is counter clockwise

  - Compatibility with nitrogen and flushing agents

  - Demonstrate the flush and pigging for class

### Activity Part 2: Watch the Solvent Flush Video (15 minutes)

Video:

Have the class watch the videos on how to use the solvent flush (PPT slide #X)

- How to use Nu-Calgon's Rx11-flush

- RX11 Micro Training

  - (Start video at 5:00 and end at 7:47)

### Activity Part 3: Rx11 Solvent Flush (10 minutes)

Instructor-led demonstration:

- Create a slight restriction on the outlet point of the line set

- Connect Rx11 injection valve

- Flush solvent through the entire line set

  - 20 - 30 seconds ⅜” line per 50’ of line set

  - 60 - 90 seconds ¾” & ⅞” line per 50’ of line set

- Maintain flow velocity sufficient to carry contaminants (as per project specification).

- Collect discharged solvent into approved containers

- Continue flushing until solvent appears visually clean and free of debris

- Completely drain remaining solvent from the line set

Quality Criteria:

- No visible particulate, discoloration, or oil residue in discharged solvent.

### Activity Part 4: Hilmor Line Set Cleaner Tool Pigging (10 minutes)

Instructor-led demonstration:

- Cut pipe restrictions off of line sets ends

- Use a reamer tool to deburr the inside of both ends of any lines being cleaned

- Place the catch device at the end of the lines where the foam pig will exit

- Select the correct nozzle sizes to fit the lines being cleaned

- Attach the selected nozzles to the lines by placing the clear hose side of the nozzle      over the end of the line set opposite the catch device and tightening thumbscrew clamps      hand tight

- Select the cleaning pigs to fit the line set sizes being cleaned

- Attach the trigger assembly to the nozzle

- Place an appropriately sized foam pig into the loading chamber

- Close the loading chamber by sliding forward and latching

- Using a standard 1/4” refrigerant hose:

  - Connect the trigger assembly fitting to a nitrogen cylinder through a regulator

  - Set regulator to a maximum pressure of 60 psig

- Squeeze the trigger and launch the foam pig through the line:

  - Verify the end of the line where the foam pig will exit from is not pointed directly at anyone, as this may result in injury during operation

- Repeat the load and launch process until the pig comes out clean

- Move trigger assembly to the next nozzle and repeat process

- Place electrical tape on both ends of the line sets to prevent recontamination

## Common Mistakes Discussion (5 minutes)

Instructor reviews common mistakes when cleaning line sets:

- Insufficient nitrogen pressure

- Skipping the pigging step

- Flushing in the wrong direction

- Proper flushing duration (per manufactures instructions)

- Not being prepared for residual backflow at point of injection

- Not capping the ends of the line set with electrical tape

### Activity Part 5: Guided Practice Line Set Cleaning (15 minutes)

Each Installer completes the following:

- Use the Rx11 solvent flush on a piece

- Use the Hilmor Line Set Cleaner tool with the appropriate cleaning pig and nitrogen tank to shoot the cleaning pig through the line set

  - One end of the line set should have the pig catcher and bucket

- Blow through the line set with dry nitrogen to remove residual solvent vapors

- Clean up and re-pack the cleaning kit

### Assessment

Instructor circulates to check for the following:

- Evaluate point of entry and discharge

- Safely prepare for discharge of the Rx11 flush

- Safely prepare for discharge of the cleaning pig

- Purging the nitrogen lines long enough per manufacturer recommendations

  - Not too long or too short of time

- Nitrogen pressure set to correct PSI

Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Nitrogen Pressure Testing the System

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

4 hours

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Explain the purpose of pressure testing the system with nitrogen

- Safely connect nitrogen to the system

- Pressurize the system to manufacturer-recommended levels

- Perform a leak detection

- Interpret and troubleshoot a drop in pressure

- Properly depressurize the system after testing

## Materials & Tools (per station)

- Jetson Air System

- Systainer Kit - HOD-1

- Nitrogen cylinder w/ dual-stage nitrogen regulator

- Single valve CRT

- Dual VCRT valve

- Big Blu bubble testing leak detector

- (2) - Fieldpiece Pressure Probes

- Fieldpiece Job Link mobile application

- Safety glasses and gloves

## Safety Brief (15 mins)

Instructor reviews the Dos and Don’ts of working with compressed gas:

Nitrogen Tank Don’ts:

- Never carry a nitrogen tank up a ladder

  - Use the 50’ hose when nitrogen is needed in an attic

- Never use a tank with a damaged regulator

- Never exceed manufacturer pressure limits

  - Cylinders can be pressurized up to 2-3k psi

  - Exposure to high pressure around 100 psi can cause skin penetration

  - 1k+ psi can be very dangerous, tissue damage, infection, and internal injury

Nitrogen Tank Do’s:

- Always visually inspect cylinders, regulators, and hoses before use

  - check for leaks!

- Stand to the side of gauges

- Pressurize slowly and gradually

- Wear eye protection and gloves at all times

- Always work in a well ventilated area

- The regulator knob has to be turned completely counterclockwise before opening the cylinder valve

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- Why it’s necessary to pressure test the system

- What we learn by pressure testing the system:

  - If we have any leaks

  - Integrity of the flare joints and press joints

- Pressure testing new line sets vs. re-used line sets

- What it means if you lose pressure during a test

- If pressure is lost, how do we locate the leak

Check for Understanding:

- “What happens if moisture or oxygen enters the system?”

- “Why do we use nitrogen instead of compressed air or oxygen?”

- “Why is maintaining your equipment so important?”

- Why is it important for the system to hold pressure?

### Activity Part 2: Watch the Pressure Test Video (35 minutes)

Video:

Have the class watch the video on how to leak test with nitrogen pressure (PPT slide #X)

- How to Leak Test an AC With Nitrogen Pressure

- How to Recover, Vacuum, and Charge an HVAC System | Step-by-Step Guide

  - Watch the video from beginning to 27:00

### Activity Part 3: System Preparation (15 minutes)

Instructor asks:

- Why is it important that all connections or joints are exposed during the pressure test?

- Why do we try to minimize the number of press fit connections?

- Using Notion, who can tell me what the torque specs are for the flare nuts on service valves on ¾” and ⅜” line sets?

Instructor-led demonstration:

- Confirm system line set’s press fit connections are properly pressed, exposed, and the depth gauge marks are visible

- Confirm system line sets flare connections are properly torqued at the IDU and ODU:

  - 60 ft lbs for ¾ line

  - 26 ft lbs for ⅜ line

- Confirm o-rings in testing equipment are in place and in good condition

  - Replace if damaged

- Ensure service valves are positioned correctly

Instructor asks:

- “Using Notion, who can tell me the difference between “back seated” and 
“front seated” valves?”

Instructor explains:

- It’s important to know the difference between front seated and back seated valves.

  - Front Seated = Attached unit is fully isolated

  - Back Seated = Attached unit is open to the rest of the system

- If the system ships with a charged ODU, then the valves are "front seated" which means they’re fully closed.

- The ODU valves should remain front seated while the rest of the line set is prepped (pressure tested, vacuumed and charged), before the valves are opened and fully backseated.

- We have seen some situations where pressure testing "pushes" past the closed valve into the coil, mixing nitrogen with the refrigerant. It’s critical that the tech confirms that the valve is fully front seated before doing the pressure test to prevent this from happening.

### Activity Part 4: Nitrogen Cylinder Setup (15 minutes)

Instructor-led demonstration:

- Secure nitrogen cylinder (upright)

- Attach regulator

- Attach dual valve VCRT with site glass to the ¾” service valve at the ODU (make sure valves are in the OFF position

- Attach the single valve VCRT to ⅜” service valve at the ODU

- Remove Shrader valves from both VCRTs

  - Do NOT lose the Shrader valves stems!

  - Stick valve stems to the side ODU (they’re magnetic)

- Attach one end of the YELLOW hose to the nitrogen regulator

- Attach the other end of the YELLOW hose to the end port of the single valve VCRT connected to the ⅜” liquid line of the ODU.

- Attach the Fieldpiece Pressure Probe to the branch side of the dual valve VCRT

Instructor explains:

- Purge before pressurizing

- Never introduce air into the system

### Activity Part 5: Connecting the Fieldpiece Probes to the Fieldpiece
Mobile App (10 minutes)

- Turn on the Fieldpiece pressure probe

- Ensure pressure probe is on the high side setting (red indicator at the bottom)

- Open the Fieldpiece app:

  - Tap ‘MEASUREMENTS’

  - Tap the icon with a square and a down arrow (3rd from left at the top)

  - Scroll to the bottom

  - Tightness (N2 Test)

  - Tap the ‘LINK TOOL’ button in the app to link the app to the pressure probe

  - Select the pressure probe

  - Press ‘START’

### Activity Part 6: Pressurizing the System (45 minutes)

Instructor-led demonstration:

Pressurizing the System with Nitrogen

- Ensure all VCRT valves are closed (except the branch port valve on the dual VCRT)

- Ensure the nitrogen regulator knob is turned all the way counterclockwise

- Open the nitrogen cylinder valve

  - Slowly turn the regulator knob until the downstream pressure starts building (approx. 20 - 30 psi)

- Open the ⅜” VCRT port valve

- Open the ¾” VCRT port valve until the pitch of the air exiting the suction VCRT changes (30 - 45 seconds)

- Close the ¾” suction side VCRT valve

Pressure Testing the System

- Open the pressure regulator knob until the regulator gauge reads 200 psi

- Open the ⅜” liquid line VCRT valve

- Wait until the pressure rises to 200 psi on the Fieldpiece app

- Soap test all line set press fit joints and flares:

  - If bubbles form, there is a leak:

    - Release pressure and correct the leak

    - Repeat from step 2

    - If the test at 200 psi is successful, move onto step 5

- Close the ⅜” liquid side VCRT valve

- Increase the pressure on the regulator to 550 psi

- Open the ⅜” liquid side VCRT valve

- Monitor the Fieldpiece app until 550 psi is reached

- Shut off  ⅜” liquid side VCRT valve

- Shut off the nitrogen tank valve

- Remove the YELLOW hose

- Inspect all press fit joints and flares for bubbles

- In the Fieldpiece App, start the N2 Tightness Test

- Monitor for 30 minutes, monitoring for pressure drop

Instructor asks:

- Using Notion:

  - Why do we wait 30 minutes?

  - What is system pressure decay?

  - How do you troubleshoot pressure decay on a Jetson Air system?

### Activity Part 7: Depressurizing the System (10 minutes)

Instructor-led demonstration:

- Once the system is confirmed to be leak free, carefully depressurize the system by opening both VCRT valves and letting the nitrogen vent into the atmosphere.

- Monitor the Fieldpiece app and close both VCRT valves when there is 5 psi remaining.

  - Leaving a little nitrogen pressure in the system will prevent air from getting into the system

  - Remaining nitrogen will get purged out right before putting the system on a vacuum

- Keep the VCRT setup attached to the ODU for use later during the vacuum test

Quality Expectation:

- Pressure test at 550 psi for 30 minutes

- No pressure drop allowed when temp is compensated for

Instructor asks:

- Why is it okay to let nitrogen vent directly into the atmosphere?

## Activity Part 8: Guided Practice (60 minutes)

## Setup (Instructor Prep)

- Divide installers into teams of 2

- Each team works on a system station

- Instructor rotates and observes

Each Installer completes the following:

- Perform safety check

- Connect nitrogen and VCRTs

- Purge hoses

- Pressurize in stages

- Reach target pressure

- Perform leak inspection

- Document pressure and time

- Depressurize the system

Instructor circulates and watches for:

- Regulator misuse

- Rapid pressurization

- Over-pressurizing

- Forgetting to purge hoses

- Poor leak detection technique

Stop unsafe actions immediately and explain why!

Group discussion:

- How much pressure drop is acceptable?

- How does temperature affect pressure?

- What does a slow drop vs. fast drop indicate?

- Why is it okay to release nitrogen into the atmosphere?

## Common Mistakes Discussion (10 minutes)

Group discussion:

- Skipping stabilization time

- Not pressurizing to 550 psi

- Over-pressurizing

- Using compressed air

- Not checking indoor coil

- Assuming “no bubbles = no leaks”

- Pressurizing too fast can damage system

- Not leak testing (saves time but increases callbacks)

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- VCRTs should remain on the systems for vacuum testing

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

### Extra Activity: Watch the Valve Core Removal Video (5 minutes)

Video:

Have the class watch the video on how to capture large valve cores (PPT slide #X)

- Improving Capture of Large Valve Cores | Fieldpiece VC1, VC1G, & VC2G

## *Instructor Note*

- The following activity will be pulling a vacuum

- This activity transitions directly into the next

- VCRTs should remain on the systems for vacuum testing

- Installers should clean up any scrap/trash in their work area to maintain a clean job site

## Hands-On Activity: Vacuum Testing a Jetson Air System

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

5 hours

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Properly set up a vacuum for a Jetson Air System

- Describe the process of performing a vacuum test on the system

- Demonstrate pulling a deep vacuum (150 microns) ensuring decay doesn’t exceed 500 microns over 15 minutes

- Demonstrate performing a deep vacuum decay (standing) test

- Interpret micron readings to diagnose leaks

- Avoid common evacuation mistakes

## Materials & Tools (per station)

- Jetson Air System

- HOD-TB

- Systainer Kit - HOD-3

- Fieldpiece vacuum pump

- Fieldpiece vacuum gauge

- FieldPiece mobile app

- Large-diameter vacuum-rated hoses (½" and ⅜")

- (1) - ¼” Dual Valve VCRT with Sight Glass

- (1) - ¼” Single Valve VCRT) with sight glass

- Metric Allen wrench set

### Safety Brief (5 minutes)

Instructor reviews:

- Never evacuate a system with refrigerant present

- Verify system passed a nitrogen pressure test before pulling a vacuum

- Confirm vacuum pump oil is clean and at the proper level

- Safety glasses and gloves

### Activity Part 1: Theory & Tool Overview (20 minutes)

During this section, the instruction should have the vacuum machine, various hoses, and the vacuum gauge to pass around to the class.

Instructor explains:

- What “pulling a vacuum” means

- Why it’s necessary to pull a vacuum on the system

- What we learn by vacuum testing the system

- Vacuum testing new line sets vs. re-used line sets

- What do we do if we lose the vacuum during our test?

- What do we mean when we say front seated or back seated

- The various components to the Fieldpiece vacuum system

- Why we use large diameter hoses to pull a vacuum (speed)

- The role of the gas ballast on the vacuum pump

- The role that the oil plays in pulling a vacuum

- The importance of inspecting the gaskets in the hose fittings

  - New gaskets are in the van

- The importance of having clean oil and when to change the oil

  - Should change the oil once a week

- How to change the oil in the Fieldpiece vacuum system

Check for Understanding:

- Can anyone tell me what a micron is?

- What happens if moisture and refrigerant are present in the system?

- Why do we vacuum test?

- What types of leaks can there be in the piping or seals?

### Activity Part 2: Watch the Vacuum Test Video (30 minutes)

Video:

Have the class watch the video on how to pull a vacuum  (PPT slide #X)

- How to Recover, Vacuum, and Charge an HVAC System | Step-by-Step Guide

  - Start video at 26:00 - 42:00

- Fieldpiece Pro Tip | Pulling a Vacuum Easier, Faster, and Better | VPX7, VC2G, MG44

### Activity Part 3: Proper Vacuum Setup (30 minutes)

Instructor-led demonstration:

- Verify ODU service valves are front seated:

  - Show front vs back seated valves

- Purge the residual pressure (5 psi) that was left in the line sets after pressure testing

- Connect ½” large-diameter vacuum hoses directly:

  - One hose from the suction port to a ⅜” port on the vacuum pump

  - One hose from the liquid port to a ⅜” port on the vacuum pump

- Install the Fieldpiece vacuum gauge to the branch of the dual core removal tool

- Confirm:

  - All valves open

- Open ballast on pump

Instructor asks:

- “Why is the micron gauge placed at the system and not the pump?”

- “What happens if Schrader cores are left in?”

- “Did you test your equipment and seals for leaks? Will it affect your test?”

- “Why is it important to change your oil regularly?”

### Activity Part 4: Connecting the Fieldpiece Vacuum Gauge to the Fieldpiece Mobile App (10 minutes)

- Turn on the Fieldpiece vacuum gauge

- Open the Fieldpiece app

  - Tap ‘MEASUREMENTS’

  - Tap the icon with a square and a down arrow (3rd from left at the top)

  - At the top use the ‘Evacuation’ function

  - Tap the ‘LINK TOOL’ button in the app to link the app to the vacuum gauge

  - Select the vacuum gauge

  - Press ‘START’

### Activity Part 5: Pulling a Vacuum (60 minutes)

Instructor-led demonstration:

- Turn ON the vacuum pump

- Run the pump until the vacuum gauge reads 3,000 microns, then close the ballast

  - Pay attention to the oil in the sight glass. Change the oil if:

    - it’s cloudy or dirty

    - The micron drop has stalled

- Once the vacuum gauge reads 150 microns shut OFF the VCRT valves to both ½” hoses.

  - If the vacuum reading immediately jumps to 500 microns (or above), the vacuum test was not performed long enough

  - Open VCRT valves again, and continue the vacuum test until the vacuum gauge reads 100 microns

  - Close VCRT valves again

- Once the vacuum has stabilized, start the decay test

- Observe the decay rate for 15 mins. It should not rise above 500 microns over 15 minutes

  - If the vacuum rises above 500 microns, but stabilizes, continue vacuum testing for a longer duration.

  - If the vacuum continues rising, this means there is a leak in the system that needs to be corrected and the vacuum test has FAILED

  - Locate and repair the leak and start the vacuum test again

- Once the vacuum test is OK, you’re ready to add refrigerant

- Leave the VCRT valves in place (you will use them to charge the system)

- Carefully remove the vacuum hoses from VCRTs by holding the valve body with one hand and loosening the hose with the other

Instructor explains:

- Why we vacuum to 150 microns and pause

- The moisture exiting the vacuum pump is vapor from inside the line set

- Rapid drop at first (atmospheric air removal)

- Slower decline as moisture is removed

- If microns stall above 500

  - Check hose connections (for tightness and hose gasket condition)

  - Verify core tools fully open

  - Check pump oil condition

Instructor asks:

- “What are the possible causes for pressure rising on the micron gauge during the decay test?”

  - System leak on piping (bad joints)

    - Test with soap bubbles

  - Damaged hose gaskets on vacuum equipment (VCRTs and hoses)

    - Visually inspect hose gaskets and replace if necessary

  - Front seated valve(s) leaking (Most unlikely cause)

    - Refrigerant leak detector at service ports

Key Point:

- Emphasize patience and timing!

  - Getting the vacuum started before taking lunch

  - Completing other job tasks while the vacuum is running

### Activity Part 6: Guided Practice (2 hours)

## Setup (Instructor Prep)

- Divide installers into teams of 2 (4 stations)

- Each team works on a system or station

- Instructor rotates and observes

Each Installer completes the following:

- Perform safety check

- Setup and connect VCRTs

- Removal of schrader cores

- Attach vacuum hoses to system

- Start with open ballast, close at 3000 microns

- Start vacuum and run to 150 microns and hold for 5-10 minutes

- Resume vacuum and run to 500 microns and hold for 15 minutes

Instructor circulates and watches for:

- Vacuum pump misuse

- Leaving Schrader cores installed

- Measuring vacuum at the pump

- Skipping decay test

- Assuming “time on vacuum” equals dryness

Stop unsafe actions immediately and explain why.

## Assessment

- Set up vacuum pump without instructor help

- Achieve < 500 microns

- Correctly interpret decay test results

- Explain why the readings behave as they do

## Common Mistakes Discussion (5 minutes)

Group discussion:

- Having dirty oil in the vacuum pump

- Having damaged o-rings in the hoses

- Leaving the Schrader cores in

- Not using the large diameter hoses

- Not pulling below 500 microns

- Skipping the decay test

## Wrap-Up Discussion

A good vacuum isn’t about how long the pump runs—it’s about what the micron gauge tells you.”

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Properly Charging a Jetson Air System with Refrigerant

Target Audience

Entry-level to intermediate Jetson installers

Duration

3.5 hours

Group Size

2 Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Verify system readiness before charging

- Identify the correct charging method

- Calculate the correct amount of refrigerant

- Safely add refrigerant to a Jetson Air System

- Explain the importance of measuring exact refrigerant quantity (not guessing)

## Materials & Tools (per station)

- Systainer Kit - HOD-TB, HOD-3

- Refrigerant charging scale

- Fieldpiece App

- VCRTs

- YELLOW ¼” charging hose with schrader depressor removed

- A2L Reverse Thread Adapter

- (1) - 30 pound jug of refrigerant (type r454b)

- Jetson Air charging specs 0.036lb per ft/0.58 oz per ft of ⅜” line set

- 115 V Heater blanket

- 50’ Extension cord

- Fully installed and pressure tested Jetson Air System (3 ton)

- Safety glasses and gloves

## Safety Brief (5 minutes)

Instructor reviews:

- Correct refrigerant type verified

- Never mix refrigerants

- Charging cylinder secured on a level scale

- Working in a well ventilated area

- Refrigerant is very cold and can cause severe burns

- Test hoses and seals

- Service valves should be front seated

- Safety glasses and gloves

## Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor asks:

- “Why is it important that we charge the system with the proper amount of refrigerant?”

Instructor-led demonstration:

- Instructor identifies and explains the tools and materials used to charge a system:

- Scale

- Fieldpiece app

- Valve core removal tool (VCRT)

- YELLOW ¼  charging hose with schrader depressors removed.

- A2L Reverse Thread Adapter

- Refrigerant cylinder with at least 5 lbs of refrigerant.

- 115 V heater blanket

- 50’ extension cord

Instructor asks:

- Why is safety so important when working with refrigerant?

- Why is having well maintained tools so important?

- Can we reuse the same hoses we used to vacuum test to charge the system?

  - No!

- Why do we charge without schrader valves in place?

### Activity Part 2: Watch the Charging Video (20 minutes)

Video:

Have the class watch the videos on how to charge a system (PPT slide #X)

- How to Recover, Vacuum, and Charge an HVAC System | Step-by-Step Guide

  - Start video at 41:00 - to end

## Activity Part 3: Verify System Readiness (10 minutes)

Instructor-led demonstration:

- Confirm:

  - Correct line set size and length

  - System has passed a pressure test

  - System has passed a soap test

  - Service valves are front seated

Instructor asks:

- Why is measuring the line sets so important?

- Why is vacuuming the system before we charge so important?

### Activity Part 4: Weigh-In Initial Charge (30 minutes)

Instructor-led demonstration:

- Attach the YELLOW hose (with Schrader depressors removed) to the refrigerant cylinder valve  (Valve side will attach to ⅜” VCRT valve)

- Open the refrigerant cylinder valve

- Place the refrigerant cylinder on the scale upside down

  - NOTE: Canadian Installers need to keep the tank upright on the scale and use the liquid valve to connect to

- Crack the hose fitting at the single valve VCRT and purge the air from the
YELLOW hose

- Zero the scale

- Calculate Jetson-specified weight needed to be added per foot of line set ran.

  - 0.036lb per ft/0.58 oz per ft of ⅜” line set

  - line set must be measured using a tape measure (do not guess!)

- Open the VCRT shut-off valve until the system achieves the required amount of refrigerant

  - If the full amount of refrigerant can’t be drawn in by the vacuum, plug in the heater blanket and wait for the refrigerant cylinder to heat up

  - NOTE: If using the heating blanket, the cylinder must be weighed with the blanket and extension cord attached

  - Refrigerant will start flowing into the system

- Close the VCRT shut-off valve once the system achieves the required amount of refrigerant

Instructor explains:

- Proper calculations for additional line set lengths

- You’re charging both the IDU coil and the system line sets

- Importance of carefully connecting hoses and pipes

Instructor asks:

- “What if our line set was twice as long? How much refrigerant would we add?”

- “What if our line set was half as long? How much would we add?”

  - 0.036lb per ft/0.58 oz per ft of ⅜” line set

### Activity Part 5: Remove VCRTs (5 minutes)

Instructor-led demonstration:

- Carefully replace Sharader core back in ⅜” and ¾” service valves

- Remove VCRT valves

- Remove rubber seals from service valve caps

- Losely put service valve caps on service valves, soap bubble test to ensure Schrader valves are sealing correctly

- Reinstall Schrader cap seals attached to the service valve, firmly secure to compress the seal in the cap

- With allen wrench back seat service valves, soap test, replace caps on valves, ⅛” turn with crescent wrench to make sure it doesn't vibrate off

- The system is now ready for commissioning

### Activity Part 6: Guided Practice (2 hours)

Each installer group completes the following:

- Verify system readiness for refrigerant charging

- Confirm line set size and length

- Confirm the system has passed a pressure test

- Confirm the system has passed a soap test

- Confirm the service valves are front seated

- Attach hoses to refrigerant cylinder

- Attach hoses to CVRT valves

- Place refrigerant cylinder on the scale

- Crack YELLOW hose to purge air

- Open the VCRT and charge system with the correct amount of refrigerant

- Close the VCRT shut-off valve once the system achieves the required amount of refrigerant

- Remove VCRTs

Instructor circulates and watches for:

- Not correctly weighing the registrant

- Over/under charging

## Common Mistakes Discussion (5 minutes)

Group discussion:

- Not ensuring the system has been properly tested and is ready to receive refrigerant

- Not measuring or guess the length of the line sets

- Not weighing refrigerant

- Overcharging to “make pressures look good”

- Not removing the Schrader core

- Allowing air to get into the system

- Failing to allow system stabilization time

## Evaluation & Inspection

- Proper refrigerant identification

- Accurate scale use

- System performance verified

## Clean up (15 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Nitrogen Pressure Testing a 2-ton Jetson Air System

Target Audience

Entry-level to intermediate Jetson installers

Duration

4 hours

Group Size

2 Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Identify the differences between 2 ton Jetson Air and the 3, 4 and 5 ton units

- Demonstrate how to put the 2 ton Jetson Air into Vacuum mode (open EEV)

- Safely connect nitrogen to the system

- Pressurize the system to manufacturer-recommended levels

## Materials & Tools (per station)

- 2 Ton Jetson Air System

- Systainer Kit - HOD-1

- Nitrogen cylinder w/ dual-stage nitrogen regulator

- Dual VCRT valve

- Big Blu bubble testing leak detector

- (1) - Fieldpiece Pressure Probes

- Fieldpiece Job Link mobile application

- Safety glasses and gloves

### Safety Brief (5 minutes)

Instructor reviews:

- Working with pressured nitrogen

- Always visually inspect cylinders, regulators and hoses before use

  - check for leaks!

- Stand to the side of gauges

- Pressurize slowly and gradually

- Wear eye protection and gloves at all times

- Always work in a well ventilated area

- The regulator knob has to be turned completely counterclockwise before opening the cylinder valve

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- How the 2-ton Jetson Air system is different from other (3, 4 and 5 ton) units that we install.

- Why it’s important to put the 2 ton Jetson system in recovery mode

- What is an EEV?

- What effects does a EEV have on the recovery, pressure test, and charging

- How many EEVs are in a Jetson System

- Does the system need to be energized to open EEVs.

### Activity Part 2: Nitrogen Cylinder Setup (15 minutes)

Instructor-led demonstration:

- Secure nitrogen cylinder (upright)

- Attach regulator - Turn regulator control knob counterclockwise until it stops.

- Make that ⅜” flare nut on liquid line is loosely connected and not yet torqued.

- Attach dual valve VCRT with site glass to the ¾” service valve at the ODU
(make sure valves are in the OFF position

- Remove Shrader core from VCRT

  - Do NOT lose the Shrader valve core!

  - Stick valve stem to the side ODU (they’re magnetic)

- Attach one end of the yellow hose to the nitrogen regulator

- Attach the other end of the yellow hose to the end port of the dual valve VCRT connected to the 3/4” vapor line of the ODU

- Attach the Fieldpiece Pressure Probe to the branch side of the dual valve VCRT

Instructor explains:

- Purge before pressurizing

- Never introduce air into the system

### Activity Part 3: Connecting the Fieldpiece Probes to the Fieldpiece
Mobile App (10 minutes)

- Turn on the Fieldpiece pressure probe

- Ensure pressure probe is on the high side setting (red indicator at the bottom)

- Open the Fieldpiece app:

  - Tap MEASUREMENTS

  - Tap the icon with a square and a down arrow (3rd from left at the top)

  - Scroll to the bottom

  - Tightness (N2 Test)

  - Tap the ‘LINK TOOL’ button in the app to link the app to the pressure probe

  - Select the pressure probe

  - Press Start

### Activity Part 4: Pressurizing the System (45 minutes)

Instructor-led demonstration:

Purging the System with Nitrogen

- Ensure all VCRT valves are closed (except the branch port valve on the dual VCRT)

- Verify the nitrogen regulator knob is turned all the way counter clockwise

- Open the nitrogen cylinder valve

  - Slowly turn the regulator knob until the downstream pressure starts building. (approx. 20 - 30 psig)

- Open the 3/4” VCRT port valve

- Listen for air starting to purge from the loosened ⅜” flare fitting

  - Continue purge until the pitch of the escaping air changes

    - Nitrogen has now replaced all the air in the piping

    - Approx. 30 - 45 seconds

  - VERY IMPORTANT: This proves that the indoor unit EEV is open and proper pressure and vacuum tests can be performed (continue to step #6)

  - NOTE: If there’s no air flowing from the open flare nut, ensure ALL wiring is complete and IDU and ODU is powered on

  - STOP: System needs to be placed in Recovery Mode

- Close the ¾” suction side VCRT valve

- Hand tighten ⅜” flare nut and torque to 26ft.lb

Pressure Testing the System

- Open the pressure regulator knob until the regulator gauge reads 200 psi.

- Open the ¾ ” vapor line VCRT valve

- Wait until the pressure raises to 200 psi on the Fieldpiece app

- Soap test all lineset press fit joints and flares

  - If bubbles form, there is a leak

    - Release pressure and correct the leak

    - Repeat from step 2

    - If the test at 200 psi is successful, move onto step 5

- Close the ¾ ” vapor line VCRT valve

- Increase the pressure on the regulator to 550 psi

- Open the ¾ ” vapor line VCRT valve

- Monitor the Fieldpiece app until 550 psi is reached

- Shut off  ¾ “ vapor line VCRT valve

- Shut off the nitrogen tank valve

- Remove the YELLOW hose

- Inspect all press fit joints and flares for bubbles

- In the Fieldpiece App, start the N2 Tightness Test

- Monitor for 30 minutes, monitoring for pressure drop

### Activity Part 5: Putting the System in Recovery Mode (10 minutes)

Instructor explains:

If you find that the EEVs are closed when purging the system with nitrogen, you must force them open by manually putting the system in recovery mode.

Instructor-led demonstration:

- Power up the IDU

- Power up the ODU

- Confirm the communicating wire is properly wired between units

- On the ODU controller, navigate to Menu n122 — "Balance System Refrigerant"

- Select this mode, it will command both the IDU and ODU EEVs to open

- Wait — it may take a couple of minutes for the valves to fully open

- Confirm with nitrogen purge that flow is now unrestricted

- Once confirmed, shut power off

  - Shutting the power off at this point will keep EEV in an open state

- Start pressure testing process again now that EEV is open

Instructor asks:

- Using Notion:

  - Why do we wait 30 minutes?

  - What is system pressure decay?

  - How do you troubleshoot pressure decay on a Jetson Air system?

### Activity Part 6: Depressurizing the System (10 minutes)

Instructor-led demonstration:

- Once the system is confirmed to be leak free, carefully depressurize the system by opening the VCRT end valve, letting the nitrogen vent into the atmosphere.

- Monitor the Fieldpiece app and close the VCRT valve when there is 5 psi remaining.

  - Leaving a little nitrogen pressure in the system will prevent air from getting into the system

  - Remaining nitrogen will get purged out right before putting the system on a vacuum.

- Keep the VCRT setup attached to the ODU for use later during the vacuum test

Quality Expectation:

- Pressure test at 550 psi for 30 minutes

- No pressure drop allowed when temp is compensated for

Instructor asks:

- Why is it okay to let nitrogen vent directly into the atmosphere?

## Activity Part 7: Guided Practice (60 minutes)

## Setup (Instructor Prep)

- Divide installers into teams of 2

- Each team works on a system station

- Instructor rotates and observes

Each Installer completes the following:

- Perform safety check

- Connect nitrogen and VCRTs

- Purge hoses

- Open EEVs (if necessary)

- Pressurize in stages

- Reach target pressure

- Perform leak inspection

- Document pressure and time

- Depressurize the system

Instructor circulates and watches for:

- Regulator misuse

- Rapid pressurization

- Over-pressurizing

- Forgetting to purge hoses

- Poor leak detection technique

Stop unsafe actions immediately and explain why!

Group discussion:

- How much pressure drop is acceptable?

- How does temperature affect pressure?

- What does a slow drop vs. fast drop indicate?

## Common Mistakes Discussion (10 minutes)

Group discussion:

- Skipping stabilization time

- Not pressurizing to 550 psi

- Over-pressurizing

- Using compressed air

- Not checking indoor coil

- Assuming “no bubbles = no leaks”

- Nitrogen protects the system and technician

- Why is it okay to release nitrogen into the atmosphere?

- Slow pressurization prevents damage

- Leak testing saves time and reduces callbacks

- Safety is non-negotiable

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- VCRT should remain on the systems for vacuum testing

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## *Instructor Note*

- The following activity will be pulling a vacuum.

- This activity transitions directly into the next

- VCRT should remain on the systems for vacuum testing

- Installers should clean up any scrap/trash in their work area to maintain a clean job site

## Hands-On Activity: Vacuum Testing a 2-ton Jetson Air System

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

5 hours

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Properly set up a vacuum for a 2-Ton Jetson Air System

- Describe the process of performing a vacuum test on the system

- Demonstrate pulling a deep vacuum (150 microns) ensuring decay doesn’t exceed 500 microns over 15 minutes

- Demonstrate performing a deep vacuum decay (standing) test

- Interpret micron readings to diagnose leaks

- Avoid common evacuation mistakes

## Materials & Tools (per station)

- 2-Ton Jetson Air System

- HOD-TB

- Systainer Kit - HOD-3

- Fieldpiece vacuum pump

- Fieldpiece vacuum gauge

- FieldPiece mobile app

- Large-diameter vacuum-rated hoses (½" and ⅜")

- (1) - ¼” Dual Valve VCRT with Sight Glass

- Metric Allen wrench set

### Safety Brief (5 minutes)

Instructor reviews:

- Never evacuate a system with refrigerant present

- Verify system passed a nitrogen pressure test before pulling a vacuum

- Confirm vacuum pump oil is clean and at the proper level

- Safety glasses and gloves

### Activity Part 1: Theory & Tool Overview (20 minutes)

During this section, the instruction should have the vacuum machine, various hoses, and the vacuum gauge to pass around to the class.

Instructor explains:

- How pulling a vacuum on the 2-ton units is different than the 3,4 and 5 tons

- Confirming during the pressure test that the EEVs are open

### Activity Part 2: Proper Vacuum Setup (30 minutes)

Instructor-led demonstration:

- Verify ODU service valves are front seated:

  - Show front vs back seated valves

- Purge the residual pressure (5 psi) that was left in the linesets after pressure testing

- Connect ½” large-diameter vacuum hose directly:

  - One hose from the suction port to a ⅜” port on the vacuum pump

- Install the Fieldpiece vacuum gauge to the branch of the dual core removal tool

- Confirm:

  - All valves open

- Open ballast on vacuum pump (The light in the oil chamber will slow flash orange)

Instructor asks:

- “Why is the micron gauge placed at the system and not the pump?”

- “What happens if Schrader cores are left in?”

- “Did you test your equipment and seals for leaks? Will it affect your test?”

- “Why is it important to change your oil regularly?”

### Activity Part 3: Connecting the Fieldpiece Vacuum Gauge to the Fieldpiece Mobile App (10 minutes)

- Turn on the Fieldpiece vacuum gauge

- Open the Fieldpiece app

  - Tap ‘MEASUREMENTS’

  - Tap the icon with a square and a down arrow (3rd from left at the top)

  - At the top use the ‘Evacuation’ function

  - Tap the ‘LINK TOOL’ button in the app to link the app to the vacuum gauge

  - Select the vacuum gauge

  - Press ‘START’

### Activity Part 4: Pulling a Vacuum (60 minutes)

Instructor-led demonstration:

- Turn ON the vacuum pump

- Run the pump until the vacuum gauge reads 3,000 microns, then close the ballast.

  - Pay attention to the oil in the sight glass. Change the oil if:

    - it’s cloudy or dirty

    - the micron drop has stalled

- Once the vacuum gauge reads 150 microns shut OFF the VCRT valve

  - If the vacuum reading immediately jumps to 500 microns (or above), the vacuum test was not performed long enough

  - Open VCRT valve again, and continue the vacuum test until the vacuum gauge reads 100 microns

  - Close VCRT valve again

- Once the vacuum has stabilized, start the decay test

- Observe the decay rate for 15 mins. It should not rise above 500 microns over 15 minutes

  - If the vacuum rises above 500 microns, but stabilizes, continue vacuum testing for a longer duration

  - If the vacuum continues rising, this means there is a leak in the system that needs to be corrected and the vacuum test has FAILED

  - Locate and repair the leak and start the vacuum test again

- Once the vacuum test is OK, you’re ready to add refrigerant

- Leave the VCRT valve in place (you will use it to charge the system)

- Carefully remove the vacuum hose from VCRT by holding the valve body with one hand and loosening the hose with the other

Instructor explains:

- Why we vacuum to 150 microns and pause

- The moisture exiting the vacuum pump is vapor from inside the lineset

- Rapid drop at first (atmospheric air removal)

- Slower decline as moisture is removed

- If microns stall above 500

  - Check hose connections (for tightness and hose gasket condition)

  - Verify core tools fully open

  - Check pump oil condition

Instructor asks:

- “What are the possible causes for pressure rising on the micron gauge during the decay test?”

  - System leak on piping (bad joints)

    - Test with soap bubbles

  - Damaged hose gaskets on vacuum equipment (VCRTs and hoses)

    - Visually inspect hose gaskets and replace if necessary

  - Front seated valve(s) leaking (Most unlikely cause)

    - Refrigerant leak detector at service ports

Key Point:

- Emphasize patience and timing!

  - Getting the vacuum started before taking lunch

  - Completing other job tasks while the vacuum is running

### Activity Part 5: Guided Practice (2 hours)

## Setup (Instructor Prep)

- Divide installers into teams of 2 (4 stations)

- Each team works on a system or station

- Instructor rotates and observes

Each Installer completes the following:

- Perform safety check

- Setup and connect VCRTs

- Removal of schrader cores

- Attach vacuum hoses to system

- Start with open ballast, close at 3000 microns

- Start vacuum and run to 150 microns and hold for 5-10 minutes

- Resume vacuum and run to 500 microns and hold for 15 minutes

Instructor circulates and watches for:

- Vacuum pump misuse

- Leaving Schrader cores installed

- Measuring vacuum at the pump

- Skipping decay test

- Assuming “time on vacuum” equals dryness

Stop unsafe actions immediately and explain why.

## Assessment

- Set up vacuum pump without instructor help

- Achieve < 500 microns

- Correctly interpret decay test results

- Explain why the readings behave as they do

## Common Mistakes Discussion (5 minutes)

Group discussion:

- Having dirty oil in the vacuum pump

- Having damaged o-rings in the hoses

- Leaving the Schrader cores in

- Not using the large diameter hoses

- Not pulling below 500 microns

- Skipping the decay test

## Wrap-Up Discussion

A good vacuum isn’t about how long the pump runs—it’s about what the micron gauge tells you.”

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Properly Charging a 2-ton Jetson Air System with Refrigerant

Target Audience

Entry-level to intermediate Jetson installers

Duration

3.5 hours

Group Size

2 Installers

## Learning Objectives

By the end of this activity, installers will be able to:

- Verify system readiness before charging

- Identify the correct charging method

- Calculate the correct amount of refrigerant

- Safely add refrigerant to a 2-ton Jetson Air Smart System

- Explain the importance of measuring exact refrigerant quantity (not guessing)

## Materials & Tools (per station)

- Systainer Kit - HOD-TB, HOD-3

- Refrigerant charging scale

- Fieldpiece App

- (1) Dual valve VCRT

- Yellow ¼” charging hose with schrader depressor removed

- A2L Reverse Thread Adapter

- (1) - 30 pound jug of refrigerant (type r454b)

- Jetson Air charging specs 0.036lb per ft/0.58 oz per ft of ⅜” lineset

- 115 V Heater blanket

- 50’ Extension cord

- Fully installed and pressure tested Jetson Air System

- Safety glasses and gloves

## Safety Brief (5 minutes)

Instructor reviews:

- Correct refrigerant type verified

- Never mix refrigerants

- Charging cylinder secured on a level scale

- Working in a well ventilated area

- Refrigerant is very cold and can cause severe burns

- Test hoses and gaskets

- Service valves should be front seated

- Safety glasses and gloves

## Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- How charging a 2-ton units is different than the 3,4 and 5 tons

## Activity Part 2: Verify System Readiness (10 minutes)

Instructor-led demonstration:

- Confirm:

  - Correct lineset size and length

  - System has passed a pressure test

  - System has passed a soap test

  - Service valves are front seated

Instructor asks:

- Why is measuring the linesets so important?

- Why is vacuuming the system before we charge so important?

### Activity Part 3: Weigh-In Initial Charge (30 minutes)

Instructor-led demonstration:

- Attach the YELLOW hose (with schrader depressors removed) to the refrigerant cylinder valve

- Open the refrigerant cylinder valve

- Place the refrigerant cylinder on the scale upside down

  - NOTE: Canadian Installers need to keep the tank upright on the scale and use the liquid valve to connect to

- Crack the hose fitting at the dual valve VCRT and purge the air from the 
YELLOW hose. Retighten fitting when refrigerant starts to escape

- Zero the scale

- Calculate Jetson-specified weight needed to be added per foot of lineset ran.

  - 0.036lb per ft / 0.58 oz per ft of ⅜” lineset

  - Lineset must be measured using a tape measure (do not guess!)

- Open the VCRT shut-off valve until the system achieves the required amount of refrigerant

  - If the full amount of refrigerant can’t be drawn in by the vacuum, plug in the heater blanket and wait for the refrigerant cylinder to heat up.

  - NOTE: If using the heating blanket, the cylinder must be weighed with the blanket and extension cord attached

  - Refrigerant will start flowing into the system

- Close the VCRT shut-off valve once the system achieves the required amount of refrigerant

Instructor explains:

- Proper calculations for additional lineset lengths

- You’re charging both the IDU coil and the system linesets

- Importance of carefully connecting hoses and pipes

Instructor asks:

- “What if our lineset was twice as long? How much refrigerant would we add?”

- “What if our lineset was half as long? How much would we add

  - 0.036lb per ft/0.58 oz per ft of ⅜” lineset

### Activity Part 4: Remove VCRT (5 minutes)

Instructor-led demonstration:

- Carefully replace Sharader core back in ¾” service valve

- Remove VCRT valves

- Remove rubber seals from service valve caps

- Losely put service valve caps on service valves, soap bubble test to ensure Schrader valves are sealing correctly

- Reinstall Schrader cap seals attached to the service valve, firmly secure to compress the seal in the cap

- With allen wrench back seat service valves, soap test, replace caps on valves, ⅛” turn with crescent wrench to make sure it doesn't vibrate off

- The system is now ready for commissioning

### Activity Part 5: Guided Practice (2 hours)

Each installer group completes the following:

- Verify system readiness for refrigerant charging

- Confirm lineset size and length

- Confirm the system has passed a pressure test

- Confirm the system has passed a soap test

- Confirm the service valves are front seated

- Attach hoses to refrigerant cylinder

- Attach hoses to CVRT valves

- Place refrigerant cylinder on the scale

- Crack yellow hose to purge air

- Open the VCRT and charge system with the correct amount of refrigerant

- Close the VCRT shut-off valve once the system achieves the required amount of refrigerant

- Remove VCRT

Instructor circulates and watches for:

- Not correctly weighing the registrant

- Over/under charging

## Common Mistakes Discussion (5 minutes)

Group discussion:

- Not ensuring the system has been properly tested and is ready to receive refrigerant

- Not measuring or guess the length of the linesets

- Not weighing refrigerant

- Overcharging to “make pressures look good”

- Not removing the Schrader core

- Allowing air to get into the system

- Failing to allow system stabilization time

## Evaluation & Inspection

- Proper refrigerant identification

- Accurate scale use

- System performance verified

## Clean up (15 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Line Set Routing Hands On

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

3.5 hours

Group Size

4 groups of 2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Measure, route, and install refrigerant line sets inside walls or ceilings

- Maintain proper bend radius and support of line sets

- Protect line sets from abrasion and damage when routing

- Install line hide on line sets

- Match installation to a provided layout/mock-up plan

## Materials & Tools (per station)

- Systainer Kits: PT-1, HOD-TB,HOD-1,HOD-2, HID-2, HID-TB, SRT

- VF- Ratcheting Tubing Bender

- Fiberglass Fish Tape

- Kallem grip

- Deburring reamer/Chamfer

- Flaring Tool

- 3.5” Hole Saw

- Line Hide & Elbows

- 2 - ⅜’ Flare Nuts

- 2 - ¾” Flare Nuts

- Super Hawg

- Zip ties

- Steel ¾” All Round strap (HID-2)

- Duct Tape

- Line Set  ⅜” & ¾” (24 ft. left over from original roll)

- Communication Wire (21 ft)

- Tubing cutter

- Permanent marker

- Tape measure

- Safety glasses & gloves

### Safety Brief

Instructor reviews:

- Potential for cuts from sharp tubing ends

- Deburr copper tubing after cutting - sharp edges cut fingers!

- Be cautious when reaching into wall cavities

- Pinched fingers

- Correct drill use and sharp bits

- Eye injuries from debris

- Safety glasses & gloves

### Activity Part 1: Theory & Tool Overview (10 minutes)

Instructor explains:

- Running refrigerant line sets is one of the most critical foundation skills in HVAC installation.

- Before a system can be evacuated, charged, or started, the line set must be routed, protected, and supported correctly.

- A poor line set installation cannot be “fixed later” without costly rework and performance loss.

Instructor recap of how line sets work within the whole heat pump system:

A refrigerant line set is not just tubing — it is the circulatory system of the HVAC system. It must:

- Carry refrigerant efficiently

- Protect oil return to the compressor

- Minimize heat gain/loss

- Withstand vibration and movement over time

Improper routing, bending, or support can cause:

- Reduced system efficiency

- Oil return problems

- Refrigerant leaks

- Premature compressor failure

- Noise and vibration complaints

Learning correct line set installation prevents these issues before they ever reach the start-up phase.

### Activity Part 2: Planning the Route (5 minutes)

Instructor explains:

- Installers will review the line set routing diagram

- Installers need to identify the following on the lab station:

  - Shortest practical path to run the line sets

  - Where to make the wall penetrations

  - Where to make the required bends

- Installers need to be aware of potential obstructions in the ceiling:

    - Fireblock

    - Electrical wires

    - Plumbing pipe

    - Insulation

Each Installer completes the following:

- Use the line set routing diagram to determine the following:

  - Determine the line set penetration point

  - Mark the penetration locations on the mock-up

### Activity Part 3: Making Wall Penetrations (30 minutes)

Instructor explains:

Drilling from outside the home, through wood siding and into a floor joist space (rim joist/band joist cavity) needs accuracy so you don’t hit framing, wiring, or plumbing.

Instructor led-demonstration:

Locate the wall penetration point

- Verify penetration location from inside the home before drilling from outside if possible (normally from a crawl space)

  - Go inside and identify the target floor joist bay (between joists).

- Measure from a fixed reference point (corner, door frame, window, or foundation wall).

- Confirming the location will:

  - not go through a joist

  - not damage any electrical wiring

  - not damage or penetrate plumbing or gas lines

- Transfer the measurement to the exterior wall and mark the spot to drill

- If unsure, drill a small 1/8" exploratory hole first to confirm you are in an open joist space

  - Check the hole with a piece of wire to determine how close on either side the hole is to a joist

Mark the exterior drill point

- Mark the center of the hole on the siding.

- Ensure the hole will be:

  - Above grade

  - Clear of trim boards and siding seams

Safety Brief for using the Super Hawg Key

- Always position yourself:

  - Solid footing (no ladders if possible)

  - Two hands on the Hole Hawg

  - Brace drill against your body or thigh

  - If the bit binds, release the trigger immediately

  - Keep wrists straight

  - Never drill overhead without full control

- Always wear:

  - Safety glasses

  - Hearing protection

  - Gloves

NOTE: Super Hawgs are equipped with a clutch to prevent twisting. have high torque

## Prepare the Hole Saw

- Install the 3.5" hole saw with pilot bit.

- Set drill to:

  - Low speed/high torque

- Verify the arbor is tight and secure.

## Start the Cut Through Siding

- Place the pilot bit on your marked point

- Start drilling slowly until the teeth bite into the siding

- Keep drill square to the wall

## Drill in Stages

- Drill about ½ – 1 inch, then back out

- Clear sawdust from the hole saw

- Continue through:

  - Wood siding

  - Sheathing

  - Rim board

- This prevents:

  - Overheating

  - Binding

  - Splintering

## Break Through Into Floor Joist Space Carefully

- As you near the inside cavity:

  - Let the pilot bit break through first

  - Reduce pressure

  - Slow RPM

  - Stop once fully into the joist bay

NOTE: Do NOT plunge aggressively — this avoids blowing out interior material.

## Inspect the Opening

- Shine a flashlight into the hole

- Confirm:

  - Clear joist space

  - No wiring or plumbing

  - Adequate clearance for piping

Instructor asks:

- Why should you try and avoid drilling through siding seams or knots?

### Activity Part 4: Guided Practice line set Penetrations (2 hours)

## Setup (Instructor Prep)

- Divide trainees into teams of 2 on opposite sides of the wall

- Each team works on a system or station

- Instructor rotates and observes

Each Installer completes the following:

- Locate the wall penetration point

- Mark the exterior drill point

- Prepare the hole saw

- Start the cut through siding

- Drill in stages

- Break through into floor joist space carefully

- Inspect the opening

Instructor circulates and watches for:

- Safe work practices

- Proper use of the Hole Hawg

- Properly drill usage and not cutting too quickly

Stop unsafe actions immediately and explain why.

### Activity Part 5: Routing the line sets (30 minutes)

Instructor explains:

- Use fish tape to help guide line set

- Tape ends of line set to prevent contamination

- Kallem grip to attach both line sets and the communication wire to fishtape

- Maintain and guide line sets through both openings

- Secure lines:

  - Vertically, horizontal

  - At direction changes

Each Installer completes the following:

- Run the fishtape through each penetration

- Tape ends of line set to prevent contamination

- Attach line sets to the fishtape

- Attach comm wire to the line set kallem grip tool

- Route both line sets through the mock-up

- Secure line sets to the wall

- Install line hides

Instructor Coaching:

- Tips for getting the fishtape through the penetrations

- What do if the tape gets stuck

- Ensuring the line sets are properly attached to the fishtape

- Ensuring the line sets don’t get damaged

- Ensuring line sets are properly supported

- Ensuring line sets and linehides are level and plumb

### Activity Part 6: Measure and Bend line sets Part  (60 minutes)

Instructor explains:

- This is a precision line set bending and routing activity through an enclosed joist bay

- Your only access is through the holes you’ve cut in the rim joist

- This means:

  - You cannot adjust bends once routed inside the wall

  - Sequence and orientation is critical

  - Everything must stay in the same plane

## Preparing the line sets

- Using the line set routing diagram/planset, measure total run length including:

  - Vertical rises

  - Horizontal runs

  - Service loops at both ends

  - Line Hide

- Cut line set

  - Place tape on both ends to prevent contamination

- Prepare line set for bends

  - Establish an orientation line

  - Draw a straight reference line (“TOP”) along the section of the pipe that will be bent. Approx. 6’ft at each end.

  - All bends must be made without rotating off this line

## Bending the line sets

- Measure and mark from the end (wrap marks fully around pipe)

- From the end:

  - Mark 3 ft (bend #1)

  - From that mark, measure 2 ft (bend #2)

  - From that mark, measure 1 ft (bend #3)

- Draw a full circle line around the pipe at each mark

- Bend the end (in order)

  - Bend #1: 90° down

  - Rotate pipe 90° left, Bend #2: 90°

  - Rotate pipe 90° back parallel, Bend #3: 90°

- Keep the pipe aligned with the reference line. Do not over-bend.

Each Installer completes the following:

- Measure the total length from the ODU to the IDU

- Cut line sets to the appropriate length according to the drawing/planset.

- Bend linsets according to the drawing/planset

  - Bending is preferred over cutting and ProPressing

- Put correct size flare nuts on each end of the line sets

- Flare each end of the line sets

### Activity Part 7: Sealing Penetrations (10 minutes)

Instructor asks:

- Why is it important that you seal up the penetrations after you’ve run the line sets?

  - Prevents:

    - Water/moisture intrusion

    - Air leaks

    - Insects and rodents

- What do we use at Jetson to properly seal wall penetrations?

  - Exterior caulking (clear silicone)

### Activity Part 8: Terminating line sets at the Equipment (10 minutes)

Instructor should review key take-aways from the line set flaring and torquing lab:

Instructor asks:

- What is a flare nut?

- Where on the Jetson system are flare nuts used?

- Why is it important to ream the line sets?

- What do we need to put on the threads of the flare nuts before we attach them to the flare blocks on the units?

- Who remembers the torque specs for:

  - 60 ft lbs for ¾ line

  - 26 ft lbs for ⅜ line

- How many times can you re-torque a flare nut on a line set?

## Common Mistakes Discussion (5 minutes)

Group discussion led by instructor:

- Missing the joist bay with the Super Hawg

- Kinking or bending copper

- Hidden damage that leads to system failure

- Use proper bending techniques

- Never force tubing into position

- Flaring line sets before putting the flare nut on

### Quality Expectations

In the field, the quality of a technician’s line set work is often:

- The first thing inspectors and customers notice

- A major factor in callbacks

- A reflection of craftsmanship and professionalism

## Optional Advanced Variations

- Add intentional obstacles (extra studs, offset turns)

- Require code reference (local or manufacturer specs)

- Introduce time limits

- Have trainees critique each other’s installs

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris, saw dust, and scrap material

### Activity Setup (Instructor)

Prepare the mock-up

- Clearly label:

  - Indoor unit location

  - Outdoor unit location

  - Joist bay to run line sets in

  - Studs, joists, or other obstructions

  - Provide a simple drawing or taped layout that shows the intended route.

Pre-cut or full-length option

- Use of remainder of line set assigned from Unrolling Activity (Approx 29’)

## Hands-On Activity: Installing & Wiring the Jetson Hub

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

4 hours

Group Size

Individual Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Explain the purpose of the Jetson Hub

- Securely install the Jetson Hub on the IDU

- Properly install the Hub antennas in the correct orientation

- Properly remove the old thermostat and replace it with a Jetson smart thermostat

- Properly make wire connections at the hub from the following system components:

  - Thermostat

  - Temperature & Humidity sensor

  - Indoor Air quality sensor

  - Energy sensor (Emporia)

- Neatly wire manage all wires in an aesthetic manner

## Materials & Tools (per station)

- Low Voltage Training Wall w/ wiring diagram mounted on wall

- Systainer Kit HID - TB, HOD-2

  - Wire strippers

  - Precision screwdrivers

  - Phillips screwdriver

- Wire nuts

- Zip Ties

- Cable clips & wood screws

- Wagos

- 8’ shielded wire

- 16’ - 2 Wire

- 16’ - 4 Wire

- Safety glasses & gloves

- Old thermostat (non Jetson)

- 240v/24v Transformer (new air handlers have this pre-installed)

- (1) - 6 post Terminal block

- (2) - 2 post Terminal block (One to simulate condensate pump and overflow)

- Jetson Hub

- IDU Board

- ODU Board

- Temp/Humidity Board + one complete for show and tell

- IAQ sensor Board + one complete for show and tell

- Jetson thermostat and baseplate

### Safety Brief

Instructor reviews:

- PPE requirements

  - Gloves and Glasses

  - Stripping wires

- Electrical safety

### Activity Part 1: Theory & Tool Overview (30 minutes)

Instructor prompt:

- Have the class go into the Notion app

- Ask for a volunteer to read the following

“What is the definition of the Jetson Hub?”

Volunteers must explain:

- The Hub is the brains of the system

- It connects the heat pump to the sensors

- It connects the heat pump to the thermostat

- How the Hub communicates and what information it communicates

- How the homeowner uses that information

- How Jetson uses that information

Instructor-led demonstration:

The instructor should have a Jetson Hub, all of the sensors, and a thermostat on hand to show and pass around to the group.

- Identity and explain the Jetson Hub:

  - Phoenix connectors

    - Can be removed

    - Need to use a precision screwdriver

  - LED Lights

  - Hub antennas

- Identify and explain all low voltage components that interface with Jetson Hub:

  - Air quality sensor

  - Temperature/Humidity Sensor

  - Thermosat

  - Emporia

    - CT monitors whole home consumption at the main panel

  - CT clamp on one leg of IDU power

    - Explain the importance of facing the correct direction - (toward the main breaker)

Instructor asks:

- What type of wire do we use to make the connections for each of the sensors, IDU, and the ODU at the Hub?

  - The instructor should listen for the initial answers

  - Prompt the group to open the Notion app and ask Notion AI “What type of wire do I use on the hub?”

  - Have a volunteer read back the wiring specs from Notion

    - 18 Gauge 2,3,4, wire

    - 18 Gauge shielded Communication Wire

Checkpoint: Use this as an opportunity to reinforce the use of Notion in the field when they need answers to a question.

### Activity Part 2: Wiring Diagram Overview (10 minutes)

Instructor prompt:

- Provide the installers with the Hub wiring diagram

- Installers should gather at the classroom training system

- Explain and compare the wiring diagram with the layout on the training board

- Call out the different wire types used

- Explain the purpose of the dip switch and how to properly set it

- Call out the wire management and the importance of:

  - Aesthetics

  - Serviceability

  - Workmanship

  - Correct Wire stripping

### Activity Part 3: Guided Practice Wiring the Jetson Hub (90 minutes)

Each installer completes the following:

- Use the wiring diagram to make all wire connection at the Jetson Hub on the low voltage wiring wall

- Replace the old thermostat and baseplate with the Jetson thermostat and baseplate

- All sensors must be terminated in the correct positions on the Hub

- All sensors must be wired with the correct wire gauge/type

- All wires must be stripped to the correct strip length

- Wiring must be neatly managed using wire management clips

Instructor circulates to ensure the following:

- Wires terminated as specified on the wiring diagram

- Wires are stripped properly

  - Importance of using the correct size on the stripper

  - Wires should not be nicked, damaged or have stray wires

- Wires are securely seated in the phoenix connectors (do a tug test)

- Drain wire grounded on one end

- No loose wire strands are hanging out of the phoenix connectors

- Wire management is neat

- Proper consideration of strain relief on all wires (not too tight)

- Jetson thermostat is mounted level on the wall

- The Hub needs clean, tight, neat, undamaged wiring and connections to work correctly, if not done correctly it will create communications issues and slow the installation significantly

Checkpoint:

- Each installer must wire the training wall at least three times.

- Track the time it takes the installers to build each of the transitions to show their skill progression.

Instructor asks:

- What do you think the LED lights on the Jetson Hub mean?

  - Prompt the group to open the Notion app and ask Notion AI “What do the LED lights on the Jetson Hub mean?”

  - Have a volunteer read back the various LED blink sequences and what they mean from Notion.

Checkpoint: Another reinforcement for using Notion to get quick answers to frequently asked questions.

Opportunity for a competition:

- In a test-like format, list several questions that installers submit to Slack every day.

- Give them x amount of time to find the answers to all the questions by consulting Notion.

## Common Mistakes Discussion (5 minutes)

Instructor-led discussion:

- Not setting the dip switches

- Incorrect/backwards wiring

- Drain line on the shielded wire connected on both sides

- Wires not stripped enough/too much

- Loose strands of wire hanging out of the terminals

- Poor wire management

- Pulling wires too tight and created strain on the terminations

## Debrief & Key Takeaways (5 minutes)

Group discussion:

- Importance of making sure the wires are secure in the connectors

- Importance of proper strip length to ensure proper metal to metal connection inside the phoenix connector

- Tug test after you’ve made your connections

- Why aesthetics with your wire management matter

- Troubleshooting connections if you encounter issues with sensors

- Using Notion to find answers to FAQs

## Clean up (15 minutes)

Installer groups should work together to complete the following:

- Unwire the wall

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Hands-On Activity: Provisioning and Jetson Hub

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

60 minutes

Group Size

2 Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Define what it means to provision a Jetson Hub

- Demonstrate how to properly provision a Jetson Hub

## Materials & Tools (per station)

- (1) - Provisioning Phone

- (1) - Jetson Installer app

- (1) - Jetson Account

- (1) - Jetson Hub

- (1) - Short hub antenna

- (1) - Long hub antenna

- (1) - Jetson 24 V wall transformer

- (1) - USB-C X USB Micro cable

- (1) - Small paper clip

### Safety Brief

Instructor reviews:

- Only use equipment as intended

- Safety gloves and eye protection

### Activity Part 1: Theory & Tool Overview (20 minutes)

Instructor prompt:

- Have the class go into the Notion app

- Ask for a volunteer to read the definition of the following:

“What does it mean to provision a Jetson System?”

Volunteers must explain:

- Provisioning a Jetson Air System means to register and configure the Jetson Hub (and any connected devices) for a specific customer installation, so Jetson’s backend and apps know which home/system it belongs to and what equipment it should control.

- In practical field terms, provisioning typically includes:

  - Associating the hub to the correct address/home (so the system shows up correctly in Jetson services and the homeowner app can find it).

  - Loading a customer-specific configuration onto the hub using the Jetson installer app (often phrased as “provision hub with config”)

  - Making sure the provisioned config matches what was actually installed (e.g., Jetson Air vs Mr Cool), otherwise the hub may not communicate correctly and you may need to re-provision after the config is fixed.

- Provisioning is not the same as connecting to Wi‑Fi (that is a separate step usually done in the homeowner app), but the two are closely related during startup.

The instructor should have the following components available to pass around during the overview.

Instructor explains:

- Explain the accessories of the Jetson Hub:

  - Jetson Hub

  - Antennas

    - Long

    - Short

  - USB Cables

  - Transformer

  - Hub power port

  - Wire terminals

  - Reset button

### Activity Part 2: Provisioning the Jetson Hub (30 minutes)

Instructor-led demonstration:

Provisioning Pre-req - Configure the Jetson Air

- Confirm the Hub is wired per the Jetson Air wiring diagram

- On the IDU:

  - Set SW8-1 = ON (enables MODBUS comms to the Hub)

  - Set ENC1 rotary dial = 1

  - NOTE: If you change SW8-1 or ENC1 while the unit is powered, power cycle the IDU

Provisioning Pre-req - Initialize the Jetson Hub

- Unplug the Temp/Humidity sensor from the Hub

- Power ON the Hub

- Wait approx. 3 minutes, or until the Hub LED stops showing 5 red flashes

- Plug the Temp/Humidity sensor back in

- Wait approx. 3 minutes, or until the Hub LED stops showing 4 red flashes

- Confirm LED state:

  - it should be flashing blue (ready for Wi‑Fi setup/not connected yet)

Provisioning the Hub - Installer App

- Connect the Installer Phone to the Hub via the USB cable

- Open the Jetson Installer app

- Select the correct customer/address

  - NOTE: if you do not have the correct customer/address reach out to #field-tech-support Slack channel to have the system added

- Follow the prompts in the Installer app to Provision the Hub (often shown as “Provision Hub with config”)

  - Use a paper clip and press the “BUTTON” at the bottom of the Hub.

  - LED should turn solid blue

  - In the Jetson App, press “Provision Hub” at the bottom of the screen.

NOTE: When provisioning completes, the board may reboot and the app may show “No Hub Detected” immediately after, this is expected behavior.

Connect the Hub to the Homeowner’s Wi-Fi - Homeowner App

- Have the homeowner download and login to the Jetson Home app

- In the Jetson Home app, select the following:

  - Home icon → Home Settings → Configure Wi‑Fi

- Choose the Wi-Fi network and enter password

  - NOTE: The Hub requires a 2.4 GHz Wi‑Fi connection (not 5 GHz)

- Wait for confirmation in the app

Wait for the Hub Firmware Update to Complete (Critical for Jetson Air Systems)

- Within 5 minutes of setting up the Wi‑Fi connection, the Hub will download and install a firmware update

- During the update, the Hub LED should turn solid white.

  - NOTE: Do NOT power cycle the Hub when the LED is white

- After the Hub reboots you should see:

  - Meaningful IDU values

  - Any Hub Communication faults clear

Re-provision the Hub After the Firmware Updates (Yes, Again!)

- Re-provision the Hub with the installer app again

- Re-enter Wi‑Fi credentials with the homeowner app again (if prompted)

Final Confirmation of Successful Provisioning

- The system should now be controllable via the Jetson Home app or the thermostat

- If it’s cold outside, the system can take up to 20 minutes to fully warm up and deliver 
hot air

### Activity Part 3: Provisioning Troubleshooting (10 minutes)

Instructor Explains:

Once the Hub is powered on, you can use its LED state to confirm system status and determine if it’s set up or still needs provisioning:

- Solid green: Hub is “all good” and provisioning was successful

On the Jetson Hub, blue LED codes show connectivity states

Single Blue Solid LED = Provisioning did not Stick. What to do (field steps):

- Re-run provisioning, check for specific blocker messages:

  - Address not showing (config missing)

  - Hub already connected to another unit

  - Both need Tech Support through the #field-tech-support Slack channel

Single Blue Blinking LED = Local Network Connection Missing.  
What to do (field steps):

- Confirm the customer’s Wi‑Fi is working (phone can load a webpage on the same network).

- In the Jetson Home app, go to Home Settings → Configure Wi‑Fi and retry Wi‑Fi setup.

- Make sure you are using a 2.4 GHz network (5 GHz is not supported). If the customer’s phone is on 5 GHz, select Other and type the 2.4 GHz SSID + password manually.

- If signal is weak at the Hub location, temporarily move the Hub closer to the router for commissioning, or plan for an extender

2 Blue Blinking LEDs = Internet Connection Missing. What to do (field steps):

- You are connected to the router, but the router likely has no internet.

- Have the customer confirm the internet is up (try another device on Wi‑Fi)

- Power cycle modem/router if needed, then retry Wi‑Fi setup in the app

3 Blue Blinking LEDs = Failure to Connect to Jetson Services. What to do (field    steps)

- Confirm the internet is working first (if not, fix that)

- Retry Wi‑Fi setup

- If connection issues persist, treat it as “Hub cannot reach Jetson cloud” even though the network is up. At that point, you can’t fully finish cloud-dependent setup, and you should escalate in #field-tech-support with the address and the issue you’re seeing

Single White Blinking LED = Applying an Over-the-Air (OTA) Update. What to do (field steps):

- Do NOT reboot or power OFF the Hub

  - Leave the Hub powered ON while the update runs

- Wait until the LED state changes:

  - You are waiting for it to finish the firmware update and transition to another normal LED state (for example, solid green, solid blue, or blue blink codes)

- After the white blinking stops, continue normal setup:

  - Proceed with provisioning/Wi‑Fi setup steps based on the new LED state:

    - Solid blue = provisioning mode

    - Blinking blue = connectivity states

    - Blinking red = comms errors, etc.

- If the Hub stays blinking white for an unusually long time, do NOT power cycle during the update

🔴Single Red Blinking LEDs = Thermostat Communication Failure. What to do (field steps):

- Verify the following:

  - Hub ↔ Thermostat wiring matches the diagram

  - Wire connections are fully seated and tight  (and wires are fully seated/tight)

- Confirm thermostat wire polarity is correct

- Power cycle the Hub

  - Remove 24V power, wait 10 seconds, then restore power

- If error persists after re-checking wiring and polarity, contact #field-tech-support in Slack with the issue you’re seeing (and ideally a photo of the wiring/LED pattern)

🔴🔴 2 Red Blinking LEDs =  AHU Communication Failure What to do. (field steps):

- Verify the following:

  - Hub ↔ IDU comm wiring (D1/D2 on the IDU side) is landed correctly, tight, and not swapped/broken

- Confirm the required IDU settings for Hub comms:

  - SW8-1 = ON (enables MODBUS on D1/D2 to talk to the Hub)

  - ENC1 rotary dial = 1

  - If you change either with the IDU powered, power cycle the IDU

- Make sure the Hub firmware update has completed. During commissioning, the Hub may not talk to the IDU until firmware updates finish (you may see a blinking/solid white state during OTA)

- If error persists, post in #field-tech-support with the blink count and a photo of the wiring and dip/rotary settings

🔴🔴🔴 3 Red Blinking LEDs = Connection Issue Between the Hub and the ODU (outdoor unit). What to do (field steps):

- Verify the following:

  - Check the shielded wire run between the Hub and the ODU XYE port

  - Ensure it is actually present and landed correctly.

  - Terminations on both ends (tight, correct positions, no loose strands)

- Confirm you used shielded wire

  - If shielded wire was not used,  a new shielded wire needs to be run between the Hub and ODU

- If you only have 2-conductor available (no XYE run):

  - Newer firmware will show 3 red LEDs for this

  - The fix is still to run the proper shielded XYE cable

🔴🔴🔴🔴 4 Red Blinking LEDs = Temperature Sensor Communication Failure. What to do (field steps):

- Verify the following:

  - Hub ↔ Temp/Humidity sensor wiring (D1/D2 on the IDU side) is landed correctly, tight, and no loose strands

- Reseat/replug the Temp/Humidity sensor at the Hub and wait 30–60 seconds to see if the code clears

- If you’re also seeing 5 red blinks (AQ sensor) or multiple sensor codes, a common field fix is to unplug the sensors and bring them back one at a time:

  - Remove both sensors

  - Plug in one sensor

  - Reboot the Hub with the left reset button

  - Wait for that sensor’s code to clear

  - Plug in the second sensor

  - Reboot and wait for the next code to clear

- If error persists, swap the sensor head with a new sensor. (sensor heads can ship defective)

🔴🔴🔴🔴🔴 5 Red Blinking LEDs = Air Quality Sensor Communication Failure. What to do (field steps):

- Verify the following:

- Hub ↔ IAQ sensor wiring is landed correctly, tight, and no loose strands

- Reseat/replug the IAQ sensor and wait 30–60 seconds to see if the code clears

- If you’re also seeing both 4-red and 5-red (TH + IAQ sensor issues), a common field fix is to bring sensors online one at a time:

  - Remove both sensors

  - Plug in one sensor

  - Reboot the Hub using the left reset button

  - Wait for that sensor’s code to clear

  - Plug the second sensor

  - Reboot and wait for the next sensor code to clear

- If error persists, swap the sensor head with a new sensor. (sensor heads can ship defective)

## Common Mistakes Discussion (5 minutes)

Instructor reviews common mistakes when provisioning the system:

- Need to get some common mistakes

- Add common mistakes slide to PPT

## Hands-On Activity: Commissioning

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

4.5 hours

Group Size

2  Installers

### Learning Objectives

By the end of this activity, installers will be able to:

- Properly commissioning the Jetson Air System

- Verify proper system operation

- Troubleshoot common issues

- Record system values in the Zuper app

## Materials & Tools

- Systainer Kits - HCOMM, IDU-TB

- Operation Jetson Air  System

- Fieldpiece app

- (2) - Psychrometers

- (2) - Manometers

- (2) - Temperature clamps

- (2) - Pressure probes

- Impact drill

- Step bit

- Phillips bit

- Wrenches

- Allen keys

- Safety gloves and glasses

### Activity Part 1: Theory & Tool Overview (20 minutes)

- The instructor breaks the class into two teams

- Give each team one of the questions below and instruct them to use Notion to find 
the answer

- Give each team 5 minutes to look up their answer

- Each team will present back to the class what they learned

- The instructor should verify, correct, and elaborate on the answers provided

Question for Team  #1 - “What does it means to commission the Jetson Air System: ”

- Commissioning a Jetson Air System is an end-to-end process of proving the installation is complete, the hardware is communicating, and the system is operating correctly, then documenting it.

Question for Team  #2 - “Why is it necessary to commission a Jetson Air Smart System?”

- Commissioning is necessary because a Jetson System is not “just installed hardware.” It is a network controlled system (ODU + IDU + Hub + sensors + app/thermostat), and it only works correctly when all parts are verified to be communicating and configured correctly.

Instructor asks:

- What are the things we’re verifying when we commission the Jetson Air System?

  - The equipment can operate

  - The ODU is initialized to the IDU (ODU↔IDU comms).

  - The Hub is set up to talk to the IDU

  - The sensors are operating

  - The air quality or temp/humidity sensors are wired correctly and communicating

  - The hub is tied to the home, connected to Wi‑Fi, and updated so the app/thermostat can reliably control the system

### Activity Part 2: Pre-Check Inspection (30 minutes)

Instructor asks:

What are the 5 main system pre-checks we should confirm before we commission the system?

- Control wiring completed per wiring diagram

- Dip switches and dial set per wiring diagram

- All service valves are back seated

- Power (240 V) confirmed at the IDU and )DU

- Emporia is connected and CT clamp oriented correctly

Instructor asks:

- What happens if the dip switches and dial are not set correctly?

- What are the correct SW8-1 and ENC1 settings for hub comms, and what do you do after changing them?

  - Set SW8-1 = ON and ENC1 = 1 for Jetson Air hub communication

### Activity Part 3: System Preparation (60 minutes)

Instructor-led demonstration:

System Initialization

- Verify IDU and ODU are powered ON

- On the ODU, press the two middle buttons for 5 seconds to enter the initialization flow

- When the ODU shows 01 - 0, press OK (ODU is told the IDU is VRF)

- When the ODU shows 02 - 1, press OK (ODU is told to look for 1 IDU)

- Wait 5 – 10 minutes while it displays INIT / AuAd

- “Done” state:

  - ODU displays 0 1

Commissioning Prep

- Drill two ⅜” holes in the supply plenum downstream of the air handler (as close to the blower as practical and before major duct branches, if possible) for the TESP and temperature rise test probes

- Drill one ⅜” hole in the return air drop for the temperature rise test probe

- Hardware setup:

  - Power on: Press and hold the power button for 1 second until the LED blinks green, indicating normal operation.

  - Set side switches: For the pressure probes and the temperature clamps, use the physical switch to select:

    - Red (high side/liquid line)

    - Blue (low side/suction line)

  - Prepare Psychrometers: Remove the protective yellow caps to expose the sensors before placing them in the airstream. (NOTE: keep caps and re-install after use)

  - Manometers:  Zero out P1 and P2 (per Fieldpiece procedure)

    - Quick Tap the ON/OFF button to zero out the probes

    - Confirm 0.00 in. w.c. for both probes in the app before proceeding

### Activity Part 4: Connecting the Fieldpiece Probes to the Fieldpiece app 
(10 minutes)

Instructor-led demonstration:

Sync Probes

- Open Fieldpiece app

- Tap the ‘MEASUREMENTS’ button in the app.

- Tap ‘LINK TOOL’ in the cell where you want the reading to appear.

- Select the desired tool from the list by clicking the circle next to its ID number.

- Favorite the tool by tapping the heart icon so it connects automatically in the future.

Tool Placement and Calibration

- Pressure Probes:

  - Attach directly to VCRT end ports. They will auto-calibrate at startup if open to the atmosphere.

- Temperature clamps:

  - Attach directly to the copper lines right next to the flare nuts.

- Psychrometers:

  - Use the magnetic tips to secure the probes to the supply and return ducts after inserting the sensors into the ⅜ “ holes prepared earlier.

- Manometer Probes:

  - Insert the P1 probe into the supply ⅜” test port hole in the supply air plenum with the probe arrow facing the blower

  - Open filter slot on the AHU. Ensure the correct filter is installed

  - Remove the metal pitot tube tip, and insert the open end of tubing attached to the P2 Probe into the filter slot DOWNSTREAM of the filter

  - Loosely attach the filter cover back in place

### Activity Part 5: Perform Static & (DT) Temp Tests (30 minutes)

Instructor-led demonstration:

Total External Static pressure (TESP) check

- Set Fan speed to 3 and set temperature on the Jetson Air Thermostat to 15 - 20 degrees above/below current temperature (depending on if your running in heating or cooling - depending on season)

- Read and record the TESP from the Fieldpiece app in Zuper

- Turn the system ON and run it at full speed (high fan/max capacity)

- Read and record the Delta P from the Fieldpiece app in Zuper

Air Side Temperature Verification

- Once airflow and temps stabilize and reach their maximum temperature rise/drop (depending on mode) take the following measurements in the fieldpiece app:

  - Supply air dry bulb temperature

  - Supply air wet bulb temperature

  - Return air dry bulb temperature

  - Return air wet bulb temperature

- Record all values in the Zuper - Commissioning Form

Key Points:

- The manometer must be pointed in the direction of its receiving airflow (wrong orientation gives false readings)

- Looking for 40-45 degree F temperature rise

- Keep probes stable as to not move around

### Activity Part 6: Remove Probes (30 minutes)

Instructor-led demonstration:

Remove Probes and Seal Holes

- Remove all probes

- Plug the (3) ⅜” holes with duct plugs (located in HCOMM systainer)

- Tighten down the filter cover

### Activity Part 7: Guided Practice Commissioning the System (60 minutes)

Each installer completes the following:

- Perform Pre-commissioning inspection

  - Confirm all components are installed

  - Confirm linesets and linehides are installed

  - Check all electrical connections and terminations

  - Confirm proper cleanrances

  - Check ductwork connections and sealing

  - Inspect condensate drain

- Perform Initialization Verification

  - Verify power supply

  - Initialize system

  - Conformation system code “Done” State 0 1 displayed

- Perform System Tests

  - Drill and insert supply psychrometer

  - Drill and insert return psychrometer

  - Drill and insert supply manometer

  - Insert manometer tip into the filter slot downstream of the filter

  - Record readings in Zuper

Instructor circulates to ensure the following:

- Patients in initialization and testing

- Correct sensor/probe locations

- Correct probe orientation/positioning

- Correct tool usage - Safety!

## Debrief & Key Takeaways (15 minutes)

Group discussion:

- Did you encounter any challenges during initialization?

- Did you encounter any challenges during commissioning?

- Which steps do you need practice with?

- What, if anything, would you do differently next time?

- What are the most critical measurements taken during commissioning?

- When should you NOT proceed with system startup?

- What documentation must be completed?

## Common Mistakes Discussion (5 minutes)

Instructor reviews common mistakes when commissioning the system:

- Energizing the system before all electrical checks are complete

- Not stopping and addressing any issues before continuing the commissioning process

- Not taking your time during the commissioning process (patience is important!)

  - Sometimes the system takes a while to initiate

  - Sometimes you may not hear anything during initialization but it is performing its cycles!

- Interrupting power while the system is in INIT/auAd

- Attempting to commission the system before the ODU unit is NOT displaying 0 1

## Clean up (5 minutes)

Installer groups should work together to complete the following:

- Put away and organize all tools/systainer kits

- Put away and organize all parts and materials

- Unassemble any reusable work stations

- Clean up work area of debris and scrap material

## Role-Play Activity: Jetson Installer Departing the Jobsite

### Target Audience

Entry-level to intermediate Jetson installers

### Duration

60  minutes per group

## Presentation Deck - (Slides XX)

## Learning Objectives

By the end of the activity, the installer will be able to:

- Complete the post-installation walk-through with the customer

- Ask respectful clarifying questions

- Respond calmly to basic homeowner concerns

- Ask for a 5-star review

## Setup (Instructor Prep)

- Print out the scripts for the learners the day before this activity

- Assign homework that the installers should work in small groups to discuss and practice the scripts before class

- The installers should be prepared to role-play the scripts in class

## Roles

- Installer

- Homeowner

- Observer / Trainer / Classmates

Rotate roles so everyone practices being the installer.

## Scenario Setup

Each one of you will get to play the part of the Lead Installer.  You’ll do all the things that the Lead is supposed to do, from introducing yourself and your crew to the homeowner to explaining to the homeowner where your team is going to place the IDU and the ODU and run the lineset, to the news that you have to come back tomorrow to finish up the job.

Background given to Installer:

- You and your crew have finished installing a new Jetson Air System

- The crew is cleaning up for the day

- This is your last interaction with the homeowner and you want to ensure that they’re satisfied with the work you’ve done today

- Don’t forget to ask the homeowner for a 5-star rating

Background given to homeowner:

- The crew is finished installing the system

- You may be curious, cautious, or unsure how to operate the system

- You have a few common homeowner concerns

## Role-Play Steps

### Step 1: Transition to Walkthrough

Installer practices:

- Knocking or ringing bell

- Friendly greeting and eye contact

- Inform the homeowner that you’re finished installing their new Jetson Air System

Instructor listens for:

- Clear communication

- Polite tone

- Professional body language

### Step 2: Confirming Work is Completed

Installer should:

- Briefly explain what work was done today

- Confirm equipment was fully installed and commissioned

- Confirm equipment was tested in both heating and cooling modes

- All electrical and safety checks have been completed

- The work areas are being cleaned and cleared

Instructor listens for:

- Clearly explained all completed work

- Clearly explained the system checks that have been completed

- Confirmation that the site has been cleaned up

- Polite tone

- Professional body language

### Step 3: System Walkthrough - How to Use the System

Installer should:

- Ask the homeowner if you can come in and show them their new thermostat

- Walk the homeowner through how to use the thermostat

- Explain how heat pumps work differently than a traditional HVAC system

- Explain how to use the Jetson homeowner app

Instructor listens for:

- Clearly explained how to use the thermostat

- Clearly explained how a heat pump system operates differently than a traditional 
HVAC system

### Step 4: Outdoor Unit & Normal Operation

Installer should:

- Ask the homeowner to follow you outside to the ODU

- Explain what to expect when the ODU is operating

- If in a cold climate, explain the frost/defrost cycle

Instructor listens for:

- Clearly explained the ODU system operation

### Step 5: Maintenance & Homeowner Responsibilities

Installer should:

- Explain the maintenance responsibilities to the homeowner:

  - Changing or cleaning the air filter

  - Keeping the outdoor unit clear of snow, leaves, debris, etc.

- Explain that if the homeowner experiences any issues with their new Jetson Air System, to call us

Instructor listens for:

- Clearly explained keeping the filter clean and to regularly change it

- Clearly explained keeping the outdoor unit clear and clear

### Step 6: Comfort & Satisfaction Check

Installer should:

- Ask the homeowner, “before we leave, how does everything look and feel to you?”

Instructor listens for:

- Clearly asked if the homeowner was comfortable and satisfied with the installation

- Addressed any questions or concerns

### Step 7: Set Support Expectations

Installer should:

- Explain to the homeowner that they’ll need to fine-tune their system settings over the next few days

- Remind the homeowner again, that heat pumps operate differently than their old gas furnace, so it will be normal to need to adjust to the new system

Instructor listens for:

- Clearly explained that they may need to fine-tune and adjust their system

- Reiterated that a heat pump operates differently than a traditional gas furnace system

- Addressed any questions or concerns

### Step 8: Ask for a Google Review

Installer should:

- Ask the homeowner for a 5-star Google Review

- Offer to send them a quick link or provide them with a QR code

- If the homeowner was not satisfied with any part of the install, installer should ask probing questions to remedy the situation

Instructor listens for:

- Installer acted naturally and confidently while asking for a 5-star Review

- Addressed any questions or concerns

### Step 9: Close with Appreciation

Installer should:

- Thank the customer for trusting Jetson Home

- Let the customer know that you’re excited for the long-term benefits the customer will experience with their new system

Instructor listens for:

- Installer sounded genuine and excited for the new Jetson customer

## Observer Evaluation Checklist

Rate each item: Great Job or Needs Work

- Friendly, respectful tone

- Explained work simply

- Proud of their work and happy for customer to join the Jetson family

- Responded calmly to questions

- Explained all work that was performed and how to use the equipment

- Explained system maintenance requirements

- Professionally asked for a 5-star review

- Professional closing that includes thanking the customer for their business

## Debrief Discussion (5 minutes)

Ask the group:

- What felt natural?

- What felt awkward?

- What phrases worked well?

- What could build more trust?

- How would this change for a nervous or upset homeowner?

## Scripts - (In the participant’s Training Manual)

### Step 1: Transition to Walkthrough

“Alright, we’re all done installing your new Jetson Air System. Before we wrap up, I’d like to walk you through the system so you feel confident using it and make sure everything meets your expectations. Is now a good time to get to know your Jetson system?”

(Pause - confirm permission)

### Step 2: Confirming Work is Completed

“Here’s what we completed today:

- The system is fully installed and commissioned

- We tested it in both heating and cooling modes

- All electrical and safety checks are complete

- The work areas have been cleaned and cleared

Everything is operating exactly as designed and the system if fully engaged”

### Step 3: System Walkthrough - How to Use the System

“This is your thermostat and main control point.
For everyday use, you’ll mostly just adjust the temperature here, or you can use the Jetson App for ease of use and control.

Heat pumps work best when you keep a steady temperature rather than making frequent big changes.”

“I’d suggest that you take a look at the homeowners guide for more information on how to adjust the thermostat until you reach your ideal environment.”

“In heating mode, the system provides longer, more even heat than a traditional furnace. In cooling mode, it focuses on removing humidity first, then cooling the air.”

### Step 4: Outdoor Unit & Normal Operation

“Outside, you may notice the unit ramping up and down—that’s completely normal and means it’s running efficiently. Heat pumps don’t turn on and off like a traditional HVAC system, they gradually adjust their speed to maintain a constant temperature.

In colder weather, ice can sometimes form on the outdoor unit, this is expected and it's nothing to worry about. The system has an automatic defrost cycle, so you may occasionally see steam during defrost cycles.

Step 5: Maintenance & Homeowner Responsibilities

“As far as system maintenance goes, the main things for you as the homeowner are:

- Changing or cleaning the air filter every [X] months

- Keeping the outdoor unit clear of snow, leaves, and debris

Anything beyond that—we’ve got you covered.”

### Step 6: Comfort & Satisfaction Check

“Before we leave, how does everything look and feel to you?”

(Pause and listen. Address any questions or adjustments.)

### Step 7: Set Support Expectations

“Over the next few days, it’s normal to fine-tune comfort settings as you live with the system. If anything comes up, just reach out—we’re here to support you.

And just as a reminder, Heat Pumps work differently than your old gas furnace.

### Step 8: Ask for a Google Review (satisfied homeowner)

### “If you feel good about the install and your Jetson experience today, we’d really appreciate a 5-star Google review if you feel that we have earned it?

(Pause – customer confirm 5 Star Google Review approval)

“Great - my team and I really appreciate it!”

“It helps homeowners like you feel confident choosing us and supporting our install team directly..”

“I’ll send you a quick link or you can snap a quick pic of the QR code — it only takes about a minute.”

### Step 8: Ask for a Google Review (unsatisfied homeowner)

“If you feel good about the install and your Jetson experience today, we’d really appreciate a 5-star Google review if you feel that we have earned it?

(Pause – customer confirms less than a 5-star Google Review approval)

“Oh, that isn’t what we hoped to achieve today, can you please share with me how we missed the mark so I can remedy the situation?”

(Pause – listen for the objection, concern or issue)

Let me take care of that right away - as anything less than a 5-star Google review is not who we want to be for you”

### Step 9: Close with Appreciation

“Thank you for trusting Jetson Home and my team with your home.
We’re excited for you to enjoy the comfort, efficiency, and long-term benefits of your new Jetson Air System.”